Note to specifier: This specification section covers only “Joint Firestopping.”  Most projects require protection of through-penetrations as well; a companion section 07 84 13 “Penetration Firestopping” should be issued in addition.

SECTION 07 84 43

JOINT FIRESTOPPING

PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division-1 Specification Section, apply to work specified in this section.

1.02	DEFINITIONS

A.	Firestopping:  Material or combination of materials used to retain integrity of fire-rated construction by maintaining an effective barrier against the spread of flame, smoke, and hot gases through penetrations in fire rated wall and floor assemblies.

1.03	GENERAL DESCRIPTION OF THE WORK OF THIS SECTION

Only tested and listed firestop systems shall be used in specific locations as follows:

A.	Safing slot gaps between edge of floor slabs and perimeter curtain walls.

B.	Openings between structurally separate sections of wall or floors.

C.	Gaps between the top of walls and ceilings or roof assemblies.

D.	Expansion joints in walls and floors.

  - RELATED WORK OF OTHER SECTIONS

A.	Coordinate work of this section with work of other sections as required to properly execute the work and as necessary to maintain satisfactory progress of the work of other sections, including:

1.	Section 03 30 00 - Cast-In-Place Concrete

2.	Section 04 20 00 - Unit Masonry

3.	Section 07 84 13 - Penetration Firestopping

4.	Section 07 90 00 - Joint Protection

5.	Section 08 44 00 - Curtain Wall and Glazed Assemblies

6.	Section 09 20 00 - Plaster and Gypsum Board

7.	Section 09 29 00 - Gypsum Board

1.05	REFERENCES

A.	Underwriters Laboratories, Inc. (UL) Fire Resistance Directory, Volume II, updated annually:

1.	Joint Systems (XHBN)

2.	Perimeter Fire Containment Systems (XHDG)

3.	Fire Resistance Ratings (BXRH)

4.	Fill, Voids, or Cavity Material (XHHW)

5.	Forming Materials (XHKU)

B.	Omega Point Laboratories, Inc. (OPL) Listed Products Directory, Volume II, updated annually:

1.	Fire Resistant Joint Systems

C.	ASTM E 1966, “Standard Test Method for Fire-Resistive Joint Systems”

D. 	ASTM E 1399, “Test Method for Cyclic Movement and Measuring the Minimum and Maximum Joint Width of Architectural Joint Systems”

E.	ASTM E 84, “Standard Test Method for Surface Burning Characteristics of Building Materials”

F.	ASTM E 2174, “Standard Practice for On-Site Inspection of Installed Fire Stops”

G.	ASTM E 2307, “Standard Test Method for Determining the Fire Endurance of Perimeter Fire Barrier Systems Using Intermediate-Scale, Multi-story Test Apparatus”

H.	ANSI/UL 2079, “Tests for Fire Resistance of Building Joint Systems”

I.	International Firestop Council Recommended (IFC) Guidelines for Evaluating Firestop Systems Engineering Judgments

J.	All major building codes:  ICBO, SBCCI, BOCA, IBC and Building Code of the City of New York.

(Note to specifier: Retain or delete building codes listed above, as applicable)

- NFPA 101 - Life Safety Code

1.06	QUALITY ASSURANCE

A.	A manufacturer's direct representative (not distributor or agent) to be on-site during initial installation of firestop systems to train appropriate contractor personnel in proper selection and installation procedures.  This will be done per manufacturer's written recommendations published in their literature and drawing details.

B.	Firestop System installation shall meet requirements of ASTM E 1966 and/or ANSI/UL 2079 tested and listed assemblies that provide fire-resistance ratings not less than that of the construction in which the joint occurs.

C.	Proposed firestop materials and methods shall conform to applicable governing codes having local jurisdiction.

D.	Firestop Systems do not reestablish the structural integrity of load bearing partitions/assemblies, or support live loads and traffic.  Installer shall consult the structural engineer prior to penetrating any load bearing assembly.

E.	For those firestop applications that exist for which no tested and listed system is available through a manufacturer, an engineering judgment derived from similar tested system designs or other tests will be submitted to local authorities having jurisdiction for their review and approval prior to installation.  Engineering judgment documents shall follow requirements set forth by the International Firestop Council.

1.07	SUBMITTALS

A.	Submit Product Data:  Manufacturer's specifications and technical data for each material including the composition and limitations, documentation of tested firestop systems to be used and manufacturer's installation instructions to comply with Section 01 30 00.

B.	Submit copy of the City of New York Department of Buildings MEA Division Report for the firestop materials submitted.  MEA Division Report shall list the tested firestop system number within the report for tested systems.

(Note to specifier: Retain or delete MEA Division Report submittal requirements as set forth per Building Code of the City of New York if not applicable)

C.	Manufacturer's engineering judgment identification number and details when no tested and listed system is available for an application.  Engineering judgment shall include both project name and contractor’s name who will install firestop system as described in document.

D.	Submit material safety data sheets provided with product delivered to job-site.

1.08	INSTALLER QUALIFICATIONS

A.	Engage an experienced Installer who is certified, licensed, or otherwise qualified by the firestopping manufacturer as having been provided the necessary training to install manufacturer’s products per specified requirements.  A manufacturer’s willingness to sell its firestopping products to the Contractor or to an Installer engaged by the Contractor does not in itself confer qualification on the buyer.

B.	The work is to be installed by a contractor with at least one of the following qualifications:

FM 4991 Approved Contractor

UL Approved Contractor

Hilti Accredited Fire Stop Specialty Contractor

C.          Installer shall have not less than 3 years experience with fire stop installation.

1.09	DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials undamaged in manufacturer's clearly labeled, unopened containers, identified with brand, type, and UL or OPL label, where applicable.

B.	Coordinate delivery of materials with scheduled installation date to allow minimum storage time at job-site.

C.	Store materials under cover and protect from weather and damage in compliance with manufacturer's requirements, including temperature restrictions.

D.	Comply with recommended procedures, precautions or remedies described in material safety data sheets as applicable.

E.	Do not use damaged or expired materials.

1.10	PROJECT CONDITIONS

A.	Do not use materials that contain flammable solvents.

B.	Schedule installation of firestopping after completion of penetrating item installation but prior to covering or concealing of openings.

C.	Verify existing conditions and substrates before starting work.  Correct unsatisfactory conditions before proceeding.

D.	Weather conditions:  Do not proceed with installation of firestop materials when temperatures exceed the manufacturer's recommended limitations for installation printed on product label and product data sheet.

E.	During installation, provide masking and drop cloths to prevent firestopping materials from contaminating any adjacent surfaces.

PART 2 - PRODUCTS

2.01	FIRESTOPPING, GENERAL

A.	Provide firestopping composed of components that are compatible with each other and substrates forming joints under conditions of service and application, as demonstrated by the firestopping manufacturer based on testing and field experience.

B.	Provide components for each fire-resistive joint system that are needed to install fill material. Use only components specified by the firestopping manufacturer and approved by the qualified testing agency for the designated fire-resistance-rated systems.

2.02	ACCEPTABLE MANUFACTURERS

A.	Subject to compliance with joint systems (XHBN) listed in Volume II of the UL Fire Resistance Directory or OPL Listed Products Directory; provide products of the following manufacturer as identified below:

1.	Hilti, Inc., Tulsa, Oklahoma

800-879-8000

www.us.hilti.com

2. 	Substitution requests shall be considered in accordance with contract provisions.

2.03	MATERIALS

A.	Use only firestop products that have been tested in accordance with ASTM E 1966 and/or ANSI/UL 2079 for specific rated construction conditions conforming to construction assembly type, movement capability, spacing requirements, and fire-resistance-rating involved for each separate instance.

B.	Sealants for use with fire-resistance-rated construction joints, the following products are acceptable:

1.	Hilti CFS-SP WB Firestop Joint Spray

2.	Hilti CP 601s Elastomeric Firestop Sealant

3.	Hilti CP 606 Flexible Firestop Sealant

4.         Hilti CP 604 Self-leveling Firestop Sealant

C.	Sealants for use as part of a Perimeter Fire Barrier System between fire-resistance-rated floors and exterior wall assemblies, the following products are acceptable:

1.	Hilti CFS-SP WB Firestop Joint Spray

2.	Hilti CP 604 Self-leveling Firestop Sealant

- Pre-formed mineral wool designed to fit flutes of metal profile deck and gap between top of wall and metal deck profile; use as a backer for spray material.

- Hilti CP 777 Speed Plugs

- Hilti CP 767 Speed Strips

E.	Provide a firestop system with an Assembly Rating as determined by ASTM E 1966 and/or ANSI/UL 2079 which is equal to the fire-resistance ratings of the construction in which the joint occurs.

PART 3 - EXECUTION

3.01	PREPARATION

A.	Verification of Conditions:  Examine areas and conditions under which work is to be performed and identify conditions detrimental to proper or timely completion.

1.	Surfaces to which firestop materials will be applied shall be free of dirt, grease, oil, rust, laitance, release agents, water repellents, and any other substances that may affect proper adhesion.

2.	Provide masking and temporary covering to prevent soiling of adjacent surfaces by firestopping materials.

3.	Comply with manufacturer's recommendations for temperature and humidity conditions before, during and after installation of firestopping.

4.	Do not proceed until unsatisfactory conditions have been corrected.

3.02	INSTALLATION

A.	Regulatory Requirements:  Install firestop materials in accordance with UL Fire Resistance Directory or Omega Point Laboratories Listed Products Directory.

B.	Manufacturer's Instructions:  Comply with manufacturer's instructions for installation of construction joint materials.

1.	Protect materials from damage on surfaces subjected to traffic.

3.04	FIELD QUALITY CONTROL

A.	Examine sealed joints to ensure proper installation before concealing or enclosing areas.

B.	Keep areas of work accessible until inspection by applicable code authorities and/or independent inspection agency.

C.	Perform under this section patching and repairing of firestopping caused by cutting or penetrating of existing firestop systems already installed by other trades.

3.05	ADJUSTING AND CLEANING

A.	Remove equipment, materials and debris, leaving area in undamaged, clean condition.

B.	Clean all surfaces adjacent to sealed holes and joints to be free of excess firestop materials and soiling as work progresses.

END OF SECTION