Note to specifier: This specification section covers only “Cast-In-Place Firestop Devices for floor penetrations.”  It is ideal for projects where many repetitive holes are required in the floor construction for plumbing penetrations.  Most projects require protection of “Fire-resistive construction joints” and Wall penetrations as well; companion sections 07841 “Through-penetration firestop systems” and 07842 “Fire-resistive Construction Joints” should be issued in addition.

# SECTION 07843

# CAST-IN PLACE FIRESTOP DEVICES FOR FLOOR PENETRATIONS

# PART 1 - GENERAL

# 1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division-1 Specification Section, apply to work specified in this section.

# 1.02	DEFINITIONS

- Firestopping:  Material or combination of materials used to retain integrity of fire-rated construction by maintaining an effective barrier against the spread of flame, smoke, and hot gases through penetrations in fire rated wall and floor assemblies.

- Cast-In-Place firestop device: A device which is placed prior to placement of concrete, intended to provide the required fire resistance in the floor penetration as soon as pipe or conduit is passed through the device.  Device also acts as a water seal and a smoke seal.

# 1.03	GENERAL DESCRIPTION OF THE WORK OF THIS SECTION

Only tested firestop systems shall be used in specific locations as follows:

- Penetrations for the passage of metal pipe, insulated pipe, conduit, and cable bundles through fire-rated concrete floor assemblies.

- Repetitive plumbing penetrations in fire-rated floor assemblies.  Penetrations exist for the installation of tubs, showers, aerators and other plumbing fixtures.

# 1.04	RELATED WORK OF OTHER SECTIONS

A.	Coordinate work of this section with work of other sections as required to properly execute the work and as necessary to maintain satisfactory progress of the work of other sections, including:

1.	Section 03300 - Cast-In-Place Concrete

2.	Section 07841 – Through-penetration firestop systems

3.	Section 07842 – Fire-resistive joint systems

4.	Section 15050 - Basic Mechanical Materials and Methods

5.	Section 15250 - Mechanical Insulation

6.	Section 15300 - Fire Protection

7.	Section 15400 - Plumbing

8.	Section 16050 - Basic Electrical Materials and Methods

# 1.05	REFERENCES

A.	Test Requirements: ASTM E 814, "Standard Method of Fire Tests of Through Penetration Fire Stops"

B.	Test Requirements:  UL 1479, “Fire Tests of Through-Penetration Firestops”

C.	Underwriters Laboratories (UL) of Northbrook, IL publishes tested systems in their "FIRE RESISTANCE DIRECTORY" that is updated annually.

1.	UL Fire Resistance Directory:

a.	Firestop Devices (XHJI)

b.	Fire Resistance Ratings (BXRH)

c.	Through-Penetration Firestop Systems (XHEZ)

D.	International Firestop Council Guidelines for Evaluating Firestop Systems Engineering Judgments

E.	ASTM E 84, Standard Test Method for Surface Burning Characteristics of Building Materials.

F.	All major building codes:  ICBO, SBCCI, BOCA, and IBC.

(Note to specifier: Retain or delete building codes listed above as applicable)

G.	NFPA 101 - Life Safety Code

H.	NFPA 70 - National Electric Code

# 1.06	QUALITY ASSURANCE

A.	A manufacturer's direct representative (not distributor or agent) to be on-site during initial installation of firestop systems to train appropriate contractor personnel in proper selection and installation procedures.  This will be done per manufacturer's written recommendations published in their literature and drawing details.

B.	Firestop System installation must meet requirements of ASTM E 814 or UL 1479 tested assemblies that provide a fire rating equal to that of construction being penetrated.

C.	Proposed firestop materials and methods shall conform to applicable governing codes having local jurisdiction.

D.	Firestop Systems do not reestablish the structural integrity of load bearing partitions/assemblies, or support live loads and traffic.  Installer shall consult the structural engineer prior to penetrating any load bearing assembly.

E.	For those firestop applications that exist for which no UL tested system is available through a manufacturer, an engineering judgment derived from similar UL system designs or other tests will be submitted to local authorities having jurisdiction for their review and approval prior to installation.  Engineering judgment drawings must follow requirements set forth by the International Firestop Council.

# 1.07	SUBMITTALS

A.	Submit Product Data:  Manufacturer's specifications and technical data for each material including the composition and limitations, documentation of UL firestop systems to be used and manufacturer's installation instructions to comply with Section 1300.

B.	Manufacturer's engineering judgment identification number and drawing details when no UL system is available for an application.  Engineering judgment must include both project name and contractor’s name who will install firestop system as described in drawing.

C.	Submit material safety data sheets provided with product delivered to job-site.

# 1.08	INSTALLER QUALIFICATIONS

A.	Engage an experienced Installer who is certified, licensed, or otherwise qualified by the firestopping manufacturer as having been provided the necessary training to install manufacturer’s products per specified requirements.  A manufacturer’s willingness to sell its firestopping products to the Contractor or to an Installer engaged by the Contractor does not in itself confer qualification on the buyer.

# 1.09	DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials undamaged in manufacturer's clearly labeled, unopened containers, identified with brand, type, and UL label where applicable.

B.	Coordinate delivery of materials with scheduled installation date to allow minimum storage time at job-site.

C.	Store materials under cover and protect from weather and damage in compliance with manufacturer's requirements, including any temperature limitations.

D.	Comply with recommended procedures, precautions or remedies described in material safety data sheets as applicable.

E.	Do not use damaged or expired materials.

# 1.10	PROJECT CONDITIONS

A.	Schedule installation of cast-in-place firestop device before placement of concrete.  Schedule installation of penetrating item through cast-in-place firestop device after placement of concrete but before area is closed off or obstructed.

B.	Verify existing conditions and substrates before starting work.  Correct unsatisfactory conditions before proceeding.

# PART 2 - PRODUCTS

# 2.01	FIRESTOPPING, GENERAL

A.	Provide cast-in-place firestop devices which form a complete firestopping system without

additional caulks, sealants, or fill materials.

B. 	Provide devices which also provide a water seal, preventing movement of water floor-to-       floor along pipe or conduit.

# 2.02	ACCEPTABLE MANUFACTURERS

A.	Subject to compliance with through penetration firestop devices (XHJI) listed in Volume II of the UL Fire Resistance Directory, provide products of the following manufacturers as identified below:

1.	Hilti, Inc., Tulsa, Oklahoma

800-879-8000

www.us.hilti.com

2.	Provide products from the above acceptable manufacturer; no substitutions will be accepted.

# 2.03	MATERIALS

A.	Use only firestop products that have been UL 1479 or ASTM E 814 tested for specific fire-rated construction conditions conforming to construction assembly type, penetrating item type, penetrating item diameter requirements, and fire-rating involved for each separate instance.

B.   	Cast-in-place firestop devices for use with noncombustible and combustible pipes (closed and open systems), conduit, and cable bundles penetrating concrete floors, the following products are acceptable:

- Hilti CP 680-P Cast-In Place Firestop Device

- Add Aerator adaptor when used in conjunction with aerator (“sovent”) system.

- Hilti CP 681 Tub Box Kit for use with tub assemblies.

- Hilti CP 680-M Cast-In-Place Firestop Device for use with noncombustible penetrants

C.	Provide a firestop system with a "F" Rating as determined by UL 1479 or ASTM E 814 which is equal to the time rating of construction being penetrated.

# PART 3 - EXECUTION

# 3.01	PREPARATION

- Verification of Conditions:  Examine areas and conditions under which work is to be performed and identify conditions detrimental to proper or timely completion.

- Ensure that form work or metal deck is in place and sound at required locations to accept installation of device

- Verify location of planned penetrations through floor and mark accordingly.

3.	Comply with manufacturer's recommendations for temperature and humidity conditions before, during and after installation of firestopping.

4.	Do not proceed until unsatisfactory conditions have been corrected.

# 3.02	COORDINATION

- Coordinate location and proper selection of cast-in-place Firestop Devices with trade responsible for the work.  Ensure device is installed before placement of concrete.

- Provide adequate spacing of field run pipes to allow for installation of cast-in-place firestop devices without interferences.

# 3.03	INSTALLATION

A.	Regulatory Requirements:  Install firestop materials in accordance with UL Fire Resistance Directory.

B.	Manufacturer's Instructions:  Comply with manufacturer's instructions for installation of through-penetration materials.

1.	Protect materials from damage on surfaces subjected to traffic.

# 3.04	FIELD QUALITY CONTROL

A.	Examine sealed penetration areas to ensure proper installation before concealing or enclosing areas.

B.	Keep areas of work accessible until inspection by applicable code authorities.

# 3.05	ADJUSTING AND CLEANING

A.	Remove equipment, materials and debris, leaving area in undamaged, clean condition.

# END OF SECTION