VaporWick® Pipe Insulation      				SECTION 15083

This specification is offered as a guide to specifiers and should be employed at the discretion of the user.  The ultimate design and installation are the responsibility of the engineer or architect.

# PART 1.00 - GENERAL

1.01 	SCOPE

A.	The work covered by this specification consists of furnishing all labor, equipment, materials and accessories, and performing all operations required, for the correct fabrication and installation of thermal insulation applied to the following commercial piping systems, in accordance with applicable project specifications and drawings, subject to the terms and conditions of the contract:

- Cold Piping Systems (chilled water, brine, refrigerant), 32F (0C) to 55F (13C)

- Dual Temperature Systems, 32F (0C) to 220F (104C)

B.	The above temperature ranges are typical for these systems. However, if contract specifications call for service temperatures outside the above ranges, consult the manufacturer's published data to determine operating temperature limitations of the insulation product or products under consideration.

1.02 	REFERENCES

A. 	Thermal insulation materials shall meet the property requirements of one or more of the following specifications as applicable to the specific product or end use:

- American Society for Testing of Materials Specifications:

a. ASTM C 547, "Standard Specification for Mineral Fiber Pipe Insulation"

b. ASTM C 585, "Standard Practice for Inner and Outer Diameters of Rigid Thermal Insulation for Nominal Sizes of Pipe and Tubing (NPS System)"

c. ASTM C 795, "Standard Specification for Thermal Insulation for Use in Contact with Austenitic Stainless Steel"

B.	Insulation materials, including all closures, hangers, supports, fitting covers, and other accessories, shall be furnished and installed in strict accordance with project drawings, plans, and specifications.

1.03 	DEFINITIONS

A.	The term "mineral fiber" as defined by the above specifications includes fibers manufactured of glass, rock, or slag processed from a molten state, with or without binder.

1.04 	SYSTEM PERFORMANCE

A.	Insulation materials furnished and installed hereunder should meet the minimum thickness requirements of ASHRAE 90.1 (2001), "Energy Efficient Design of New Buildings," of the American Society of Heating, Refrigeration, and Air Conditioning Engineers.  However, if other factors such as condensation control or personnel protection are to be considered, the selection of the thickness of insulation should satisfy the controlling factor.

B.	Insulation materials furnished and installed hereunder shall have a maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with the following testing standard:

Underwriters' Laboratories, Inc.   		UL 723

1.05 	QUALITY ASSURANCE

A.	Insulation materials and accessories furnished and installed hereunder shall, where required, be accompanied by manufacturers' current submittal or data sheets showing compliance with applicable specifications listed in Section 1.02 above.

B.	Insulation materials and accessories shall be installed in a workmanlike manner by skilled and experienced workers who are regularly engaged in commercial insulation work.

1.06 	DELIVERY AND STORAGE OF MATERIALS

A.	All of the insulation materials and accessories covered by this specification shall be delivered to the job site and stored in a safe, dry place with appropriate labels and/or other product identification.

B.	The contractor shall use whatever means are necessary to protect the insulation materials and accessories (wick material, sealing tape, etc) before, during, and after installation.  No insulation material shall be installed that has become damaged in any way.  The contractor shall also use all means necessary to protect work and materials installed by other trades.

PART 2.00 - PRODUCTS

2.01 	PIPE INSULATION

A.	Molded fibrous glass pipe insulation shall comply with the requirements of ASTM C 547 and meet ASTM C 585 for sizes required in the particular system.  It shall be of a wicking type suitable for installation on piping systems as defined in section 1.01 SCOPE above. Product shall include a factory applied integral vapor retarder extending under the evaporator area of the wick and covering not less than 98% of the circumference of the product.  Exposed evaporator area shall be not less than 0.1 sq. ft./linear ft. of product.

Acceptable Manufacturers:

1. Owens Corning VaporWick® Pipe Insulation or pre-approved equal.

B.	Fittings and valves shall be insulated per manufacturer’s instructions:

- Fittings and valves shall be wrapped continuously with wicking material prior to installing insulation to ensure a continuous path for removal of condensation.

- Standard site fabricated connections (e.g. mitered, segmented, or fish mouth) are recommended for bends and fittings.

- Standard PVC fittings with blanket insulation or molded/preformed fiberglass fittings may be used.

- Standard oversizing practices shall be used for valves and flanges.

C.	All piping shall be supported in such a manner that the insulation is not compromised by the hanger or the effects of the hanger.  In all cases, hanger spacing shall be such that the circumferential joint may be made outside the hanger. Cover the evaporating holes with contractor supplied VaporWick Sealing Tape for the length of the metal saddle.

- Piping systems 3" (75 mm) in diameter or less, insulated with fiberglass pipe insulation, may be supported by placing saddles of the proper length and spacing under the insulation as designated in Owens Corning Pub. 1-IN-14210.

- For hot or cold piping systems larger than 3" (75 mm) in diameter, operating at temperatures less than +200F (93C) and insulated with fiberglass, inserts such as foam or high-density fiberglass with sufficient compressive strength shall be used to support the weight of the piping system.

- On vertical runs, insulation support rings shall be used as indicated on contract drawings.

2.02 	ACCESSORY MATERIALS

A.	Accessory materials installed as part of insulation work under

this section shall include (but not be limited to):

- VaporWick® wick material for wrapping valves and fittings

- Closure Materials – VaporWick® Sealing Tape, and mastics.

- Support Materials - Hanger straps, hanger rods, saddles, support high-density blocks, and support rings.

B.	All accessory materials shall be installed in accordance with project drawings and specifications, manufacturer's instructions, and/or in conformance with the current edition of the Midwest Insulation Contractors Association (MICA) "Commercial & Industrial Insulation Standards."

# PART 3.00 - EXECUTION

3.01 	SITE INSPECTION

A.	Before starting work under this section, carefully inspect the site and installed work of other trades and verify that such work is complete to the point where installation of materials and accessories under this section can begin.

B.	Verify that all materials and accessories can be installed in accordance with project drawings and specifications and material manufacturer’s recommendations.

C.	Verify, by inspecting product labeling, submittal data, and/or certifications which may accompany the shipments, that all materials and accessories to be installed on the project comply with applicable specifications and standards and meet specified thermal and physical properties.

3.02 	PREPARATION

A.	Ensure that insulation is clean, dry, and in good mechanical condition and that all factory-applied facings are intact and undamaged. Wet, dirty, or damaged insulation is not acceptable for installation.

B.	Ensure that pressure testing of piping and fittings has been completed prior to installing insulation.

3.03 	INSTALLATION

A. 	General

- Install all insulation materials and accessories in accordance with manufacturer's published instructions and recognized industry practices to ensure that it will serve its intended purpose.

- Install insulation on piping subsequent to painting, and acceptance tests.

- Install insulation materials with smooth and even surfaces. Insulate each continuous run of piping with full-length units of insulation, with single cut piece to complete run. Do not use cut pieces or scraps abutting each other. Butt insulation joints firmly to ensure complete, tight fit over all piping surfaces.

- For detailed installation instructions, see OC Pub No. 15-IN-44645

B. 	Fittings

- Wrap valves, fittings, and similar items in each piping system with wicking material to ensure a continuous path (100% coverage) for the removal of condensation.

- Cover valves, fittings, and similar items in each piping system using one of the following:

- Mitered sections of insulation equivalent in thickness and composition to that installed on straight pipe runs.

- PVC Fitting Covers insulated with material equal in thickness and composition to adjoining insulation.

- Seal all fitting joints with contractor supplied VaporWick Sealing Tape or approved vapor retarder mastic compound.

C. Penetrations

Extend piping insulation without interruption through walls, floors and similar piping penetrations, except where otherwise specified.

3.04 	FIELD QUALITY ASSURANCE

A.	Upon completion of all insulation work covered by this specification, visually inspect the work and verify that it has been correctly installed.  This may be done while work is in progress, to assure compliance with requirements herein to cover and protect insulation materials during installation.

3.05 	PROTECTION

A.	Replace damaged insulation which cannot be satisfactorily repaired.

B.	The insulation contractor shall advise the general and/or the mechanical contractor as to requirements for protection of the insulation work during the remainder of the construction period, to avoid damage and deterioration of the finished insulation work.

3.06 	SAFETY PRECAUTIONS

A.	Insulation contractor's employees shall be properly protected during installation of all insulation.  Protection shall include proper attire when handling and applying insulation materials, and shall include (but not be limited to) disposable dust respirators, gloves, hard hats, and eye protection.

B.	The insulation contractor shall conduct all job site operations in compliance with applicable provisions of the Occupational Safety and Health Act, as well as with all state and/or local safety and health codes and regulations that may apply to the work.