This guide specification was issued January 2010 and may be superseded without notice at any time. Therefore, please confirm that this specification is still current and has not been superseded by checking at www.cetco.com or by calling 1-800-527-9948.

CAST-IN-PLACE CONCRETE CONSTRUCTION SPECIFICATION

This guide specification has been prepared according to the principles established in the Manual of Practice published by the Construction Specification Institute and is intended for use with cast-in-place concrete structures. This specification is not intended for use with shotcrete, masonry block, or precast concrete construction. Contact CETCO regarding installation and application guidelines for Volclay Panel Waterproofing System used with below-grade shotcrete, masonry block, or precast concrete construction. CETCO, Building Materials Group – 1- 847-851-1800.

SECTION 071700  - JANUARY 2010 (Supersedes All Previous Versions)

VOLCLAY® PANEL WATERPROOFING

WITH AQUADRAIN PREFABRICATED DRAINAGE COMPOSITE

GUIDELINE SPECIFICATION FOR CAST-IN-PLACE CONCRETE

BACKFILLED WALL CONSTRUCTION

PART 1 - GENERAL

1.01	 RELATED DOCUMENTS

A.  	All of the Contract Documents, including General and Supplementary Conditions, and Division 1 General requirements, apply to the work of this section.

1.02  	WORK SUMMARY

A. 	The work of this section includes, but is not limited to the furnishing and installing the following materials, per project specifications and drawings, or as directed by bentonite waterproofing manufacturer, to cast-in-place concrete foundation walls:

1. Volclay Panel® sodium bentonite waterproofing membrane with all applicable accessory products.

2. Aquadrain® Prefabricated drainage composite and Aquadrain 100BD Base Drain

1.03	RELATED SECTIONS

A.	Other specification Sections which directly relate to the work of this section include, but are not limited to, the following:

1. Division 2: Subsurface and Geotechnical Investigations

2. Division 3: Waterstops

3. Division 5: Expansion Joint Products

4. Division 7: Joint Treatment/ Sealants, Flashing and sheet metal, and Insulation

5. Division 22: Mechanical Penetrations

6. Division 26: Conduit and other Electrical Penetrations

7. Division 31: Earthwork, Excavation and Fill

8. Division 33: Geocomposite Foundation Drainage

071700 -1

1.04 	SYSTEM DESCRIPTION

A.	Provide bentonite waterproofing and prefabricated drainage composite system to prevent the passage of liquid water and install without defects, damage or failure. Waterproofing shall consist of biodegradable corrugated kraft board containing one pound (0.45 kg) per square foot (0.1 sq m) of granular Volclay sodium bentonite.

1.05	SUBMITTALS

A.	General: Prepare and submit specified submittals in accordance with "Conditions of the Contract" and Division 1 Submittals Sections.

B.	Product Data: Submit manufacturer’s product data, with complete general and specific installation instructions, recommendations, and limitations.

C.	Product Samples: Submit representative samples of the following for approval:

1. Volclay Panel  membrane waterproofing

2. Aquadrain 15XP  and Aquadrain 100BD prefabricated drainage composites

D.	Contractor Certificate: At time of bid, submit written certification that installer has current Approved Applicator status with waterproofing material manufacturer.

E.	Waterproofing Material Warranty: At time of bid, submit a sample copy of the Manufacturer’s Waterproofing Material Warranty complete with all coverage, limitations, and conditions.

1.06 	QUALITY ASSURANCE

A. 	Installer Qualifications: Installing company should have at least three (3) years experience in work of the type required by this section, who can comply with manufacturer's warranty requirements, and who is an Approved Applicator as determined by waterproofing/drainage system manufacturer.

B.	Manufacturer Qualifications:  Bentonite waterproofing and all accessory products shall be provided by a single manufacturer with a minimum of 30 years experience in the direct production and sales of bentonite waterproofing systems. Manufacturer shall be capable of providing field service representation during construction, approving an acceptable installer, recommending appropriate installation methods of the bentonite waterproofing and prefabricated drainage system applied.

C.	Pre-Installation Conference: A pre-installation conference shall be held prior to commencement of field installation to establish procedures to maintain required working conditions and to coordinate this work with related and adjacent work. Verify that final waterproofing and waterstop details comply with waterproofing manufacturer's current installation requirements and recommendations. Pre-con meeting attendees should include representatives for the owner, architect, inspection firm, general contractor, waterproofing contractor, concrete contractor, excavating/backfill contractor, and mechanical and electrical contractors if work penetrates the waterproofing.

- Materials: Obtain bentonite panel waterproofing and prefabricated drainage materials from a single manufacturer to assure material compatibility.

- Inspection: Manufacturer’s representative shall inspect waterproofing installation periodically during application to verify that waterproofing has been installed in accordance with manufacturer’s guidelines and recommendations.

071700 -2

F.	Water Sample Test: Project site water sample supplied to manufacturer by waterproofing contractor to determine type of bentonite system (standard sodium bentonite or contaminate resistant (CR) sodium bentonite) to be utilized on the project. Manufacturer shall conduct test free of charge. Contractor is responsible for collection and shipment of 64-fluid ounces (2-liters) of actual site water. Water should be shipped in uncontaminated, sealed plastic container to: CETCO, 2870 Forbs Ave., Hoffman Estates, IL 60192, Attn: BMG Field Services. Also provide project name, city and state along with return address to forward test results.

1.07	PRODUCT DELIVERY, STORAGE AND HANDLING

A.	Delivery and Handling: Deliver materials in factory sealed and labeled packaging. Sequence deliveries to avoid delays, while minimizing on-site storage. Handle and store following manufacturer's instructions, recommendations and material safety data sheets. Protect from construction operation related damage, as well as, damage from weather, excessive temperatures and prolonged sunlight. Remove damaged material from site and dispose of in accordance with applicable regulations.

- Storage: Do not double-stack pallets during shipping or storage. Protect waterproofing materials from moisture, excessive temperatures and sources of ignition. Provide cover, top and all sides, for materials stored on-site, allowing for adequate ventilation.

1.08	PROJECT CONDITIONS

- Substrate Condition: Proceed with work only when cast-in-place concrete wall construction and surface preparation work is complete and in condition to receive waterproofing system.

B.	Weather Conditions: Perform work only when existing and forecasted weather conditions are within the guidelines established by the manufacturer of the waterproofing materials. Do not apply waterproofing materials into standing water or over ice.

1.09 	WARRANTY

A.	Waterproofing Material Warranty: Upon completion and acceptance of the work required by this section, the waterproofing materials manufacturer will provide a written five (5) year material warranty.  Issuance of Manufacturer's Material Warranty requires the following: (1) Manufacturer's Approved Applicator to install bentonite panel waterproofing system and prefabricated drainage composite. (2) In Section 3 work, Waterstop-RX must be installed 	in all applicable horizontal and vertical concrete construction joints and around applicable penetrations. Manufacturer's material warranty shall be independent from any other warranties made by the Contractor under requirements of the Contract Documents and may run concurrent with said warranties.

PART 2 - PRODUCTS

2.01 	MANUFACTURER

A.	Provide bentonite panel waterproofing with biodegradable kraft board container and applicable accessories as manufactured by Colloid Environmental Technologies Company (CETCO), 2870 Forbs Ave., Hoffman Estates, IL 60192. Phone: (800) 527-9948; (847)851-1800; Web-site: http://www.cetco.com/bmg.

071700-3

2.02 	MATERIALS

A. 	VOLCLAY BENTONITE PANEL WATERPROOFING

1. VOLCLAY TYPE 1 PANELS: Volclay Type 1 Panels consist of 1 lb. (0.45 kg) per square foot of specially treated granular sodium bentonite contained inside a biodegradable, corrugated kraft board measuring 48" x 48" x 3/16" thick (1.2m x 1.2m x 	0.47cm).

B.	ACCESSORY WATERPROOFING PRODUCTS: All accessory waterproofing materials shall be 	provided by the bentonite waterproofing manufacturer or shall have manufacturer’s written 	approval for substitution.

1. Bentoseal®:  Trowel grade sodium bentonite compound used as a detailing mastic around penetrations, corner transitions and grade terminations.

2. Hydrobar Tubes: 2” (50 mm) diameter x 2’ (60 cm) long, water soluble tube container filled with granular sodium bentonite

3. Waterstoppage®:  50 lbs. (22.7 kg) bag of granular Volclay sodium bentonite.

4. Termination Bar: Min. 1” (25 mm) wide aluminum bar with pre-punched holes on 12” (300 mm) centering for fastening.

5. CETSEAL: single-component polyether general sealant and adhesive.

6. GF-40SA: self-adhering flashing membrane used for grade and thru-wall detailing.

D.	BASE AND SHEET DRAINAGE COMPOSITE

Aquadrain® drainage composite by CETCO shall be used where specified to promote positive drainage. Use base drain accessory connectors and outlets as required.

1. Aquadrain® 15XP - 4-ft by 52-ft roll of a three-dimensional polypropylene drainage core with a nonwoven geotextile adhered to one side to allow water passage while restricting soil particles. Composite includes a thin polyethylene sheet on the back of the drainage core.

A. Compressive Strength, 15,000psf  (718 kPa); B. Water Flow Rate, 20gpm/ft (251 l/m/m);

C. Thickness,  7/16” (11 mm)

2. Aquadrain® 100BD Base Drain – 1” (25 mm) thick x 12” (300 mm) high base drain composite designed to collect water from sheet composite drainage and then discharge the water to proper sump system or gravity to daylight.

A. Compressive Strength, 10,000psf (457 kPa); B. Water Flow rate, 97gpm/ft (1,197 l/m/m);

C. Thickness, 1” (25 mm)

PART 3 – EXECUTION

A.	Comply with contract documents and manufacturer's product data, including product application and installation instructions.

3.01 	SUBSTRATE INSPECTION AND CONDITIONS

A.	The installer shall examine conditions of substrates and other conditions under which this section work is to be performed and notify the contractor, in writing, of circumstances detrimental to the proper completion of the work. Do not proceed with work until unsatisfactory conditions are corrected and are acceptable for compliance with manufacturer's warranty requirements. General substrate conditions acceptable for the waterproofing installation are listed below. For conditions not covered in this Section, contact the waterproofing manufacturer for guidance.

071700-4

B.	CONCRETE WALLS:  Cast-in-place concrete to receive waterproofing shall be of sound structural grade with a smooth finish, free of debris, oil, grease, laitance, dirt, dust, or other foreign matter which will impair the performance of the waterproofing and drainage system and which do not comply with manufacturer's warranty requirements. Volclay Panels can be installed on green structural concrete as soon as the forms are removed.  There is no product limitation regarding a minimum concrete curing time requirement for Volclay Panels to be installed over structural concrete. Manufacturer recommends gaining instructions from project structural engineer regarding any site specific concrete curing time requirement. Do not apply Volclay Panel waterproofing over lightweight insulating concrete.

1. Form fins, ridges, and other protrusions should be level and smooth with monolithic concrete surface. Honeycombing, aggregate pockets, tie-rod holes and other voids should be completely filled with non-shrink cementitious grout and level with monolithic concrete wall surface.

2.  All expansion joints should receive applicable expansion joint sealant product manufactured by others prior to the installation of the Volclay Panel Waterproofing System. Expansion joint material is the primary seal at the expansion joint and the expansion joint material manufacturer is responsible for water tightness of the joint.

NOTE: Related work to be completed under Division 3. Waterstop-RX shall be installed in all applicable vertical and horizontal concrete construction cold pour joints and around applicable penetrations and structural members secured with CETSEAL. Refer to Waterstop-RX Product Manual for further installation procedures and guidelines.

3.02 	SURFACE PREPARATION

A.	Remove dirt, debris, oil, grease, cement laitance, or other foreign matter which will impair or negatively affect the performance of the waterproofing and drainage system.

B.	Protect adjacent work areas and finish surfaces from damage or contamination from waterproofing products during installation operations.

3.03 	GENERAL INSTALLATION GUIDELINES

A. 	Install Volclay Panels with the printed side facing installer and the print oriented horizontally. Turn Panel with print vertically oriented when transitioning around inside and outside wall corners.

- Prevent bentonite waterproofing products from hydrating before material is contained with backfill. When threat of rain is imminent, installed bentonite products not already contained by backfill should be covered with polyethylene sheeting to decrease the chance of hydration. Remove polyethylene prior to overburden or backfill operations. After any precipitation, standing water should be pumped away from waterproofing as soon as possible.

C.	Hydrostatic head conditions greater than 33 feet (10 m) require the installation of two layers of Volclay Panels per Section 3.05.	 Only a single layer of Volclay Panels is required for hydrostatic pressures of 0-33 feet (0-10 m).  For hydrostatic conditions exceeding 33 feet of head pressure, install two layers of Volclay Panels as described below.

D. 	Expansion Joints: Volclay panel waterproofing is not an expansion joint filler or sealant, but may be used as an expansion joint cover over a properly installed expansion joint material placed during substrate preparation. To use Volclay Panels as an expansion joint cover, trowel 1/8" (3 mm) thick, 6" (150 mm) wide layer of Bentoseal centered over expansion joint. Install a 24" (60 cm) wide Panel strip centered over the expansion joint. Then install the main Volclay Panel course.

071700-5

3.04 	BACKFILLED CAST-IN-PLACE CONCRETE WALLS

A.     	Trowel Bentoseal over all concrete construction joints 1/8” (3 mm) thick by 3” (75 mm) wide.  Form Tie holes or recesses shall be completely filled with non-shrink cementitious grout. Trowel Bentoseal 1/8" (3 mm) thick over each grouted form tie hole.

B. 	Trowel 3/4" (18 mm) continuous fillet of Bentoseal in all inside corner transitions.

C. 	Starting at a wall base corner, bend Volclay Panel along 1/3 panel "Starter Line" (printed on panel) and install with the kraft board corrugations and print vertically oriented. Cut the Panel at the bottom edge of the "Starter Line" so that the Panel can be extended 6" (150 mm) onto the footing. Secure Panels with washer-head fasteners along each edge. After installing corner Panel, install all

succeeding Panels with kraft board corrugations and print horizontally oriented - continuing Panel onto footing minimum 6" (7.5 cm). Overlap all adjoining edges minimum 1-1/2" (38 mm).  When applicable, the base Panel course shall overlap the underslab waterproofing a minimum 6" (150 mm) to form a continuous waterproofing layer.

D. 	Stagger vertical Panel overlap joints of succeeding courses by folding the next courses corner Panel on the 2/3 panel "Lap Line" (printed on panel) and install overlapping lower Panel course minimum 1-1/2” (38 mm). After installing corner Panel, install all succeeding Panels with kraft board corrugations and print horizontally oriented - overlapping adjoining edges minimum 1-1/2" (38 mm).

E. 	Penetration. On flat surface cut Panel to fit around penetration. Immediately seal cut Panel edge by applying water with cloth or sponge prior to panel installation. After Panel is installed around penetration, trowel 3/4" (18 mm) thick fillet of Bentoseal around the penetration and extending onto Panel 1-1/2" (38 mm) at a 1/8” (3 mm) minimum thickness.

E1. 	Multiple Penetrations. Trowel 1/2" (13 mm) thick layer of Bentoseal covering entire area between penetrations and extend layer outside of penetration area minimum 3" (75 mm)  to allow Panels to overlap. At base of each penetration apply 3/4" (18 mm) fillet of Bentoseal over the main Bentoseal layer. Cut Panels and overlap Bentoseal layer a minimum 1-1/2" (38 mm).

F. 	Continue Panels up to grade detail. Terminate Panels 12" (30 cm) below finished grade elevation secured with washer-head fasteners maximum 12” (300 mm) on center to exterior of concrete wall. Per manufacturer’s detail for specific project condition(s) install GF-40SA grade flashing to primed concrete substrate with bottom edge overlapping top edge of Volclay Panels minimum 4” (100 mm). Overlap all roll ends a minimum 4” (100 mm) to form a continuous flashing. Height of flashing shall be per project details and specifications. Install a rigid termination bar along the top edge of GF-40SA; fastened maximum 12” (300 mm) on center. Complete grade termination detail with tooled bead of CETSEAL along the top edge, at all penetrations through the flashing, and all exposed overlap seams.

G. 	Before backfilling, lay Hydrobar Tubes against the base of the first Volclay Panel course at the wall/footing transition. Hydrobar Tubes should be positioned end-to-end forming a continuous line. Manually place and tamp a shovel of backfill over Hydrobar Tubes to hold them in position prior to main backfill operation.

H. 	Repair any small Panel damage by applying a 1/2” (13 mm) thick layer of Bentoseal. Repair any large Panel damage by placing a new panel into position.

I.	 Install Aquadrain prefabricated drainage composite over Panel system. Refer to Part 3.06, for Aquadrain installation instructions.

Note: Do not use Volclay Panels on masonry block walls. Consult CETCO for specific product(s) and  installation guidelines for masonry block foundation walls.

07170-6

3.05	HYDROSTATIC HEAD IN EXCESS OF 33 FEET  (10 METERS)

A.	Install two (2) Panel layers. Surface preparation, detailing, and terminations remain the same as with a single Panel layer application.

B.	Install first Panel layer with edges butted, not overlapped. Fasten butted vertical Panels securely to concrete surface with washer-headed fasteners.

C.	The second Panel layer is placed directly over the first Panel layer so that the seams of the two Panels layers stagger and do not match. The second Panel layer should mask the seams of the first Panel layer. Again, butt the second Panel layer edges together - do not overlap the Panel edges.

3.06	PREFABRICATED DRAINAGE COMPOSITE INSTALLATION

A.	 At the base of the wall, place Aquadrain 100BD (100BD) base-drain horizontally oriented with the open core side up and the 2” (50 mm) flap of fabric side tight against the wall over the previously installed Volclay Panel waterproofing using wash-head mechanical fasteners or general construction adhesive. The 2” fabric flap along the top edge of 100BD should be tightly secured against the wall. Use 100BD accessory fittings, as required, to form a continuous installation. Install 100BD discharge outlet fittings to connect to discharge pipes as required for the project.

B.	Install the bottom course of Aquadrain 15XP sheet drainage (plastic core side against the wall) with the 15XP bottom core edge in contact with open top core edge of 100BD.  Secure sheet drain to wall with washer-head fasteners. Secure extra fabric flap of 15XP extending down the top front edge of 100BD to prevent the passage of soil into the core at the connection.

C.	Install subsequent courses of Aquadrain 15XP sheet drainage in a shingle overlap style to finished grade or as shown on the project drawings. Prior to subsequent course, seal top and side core edges by tucking the products extra fabric edge flap behind the core before securing with washer-head fasteners. Install drainage sheet panels overlapped, bottom edge of higher course installed to the outside of the lower course to shed water like a roof shingle. Seal all outward overlap core edges by securing extra fabric flap with tape or general construction adhesive to filter fabric of previously installed sheet.

D. 	Around penetrations and other details, cut sheet drainage composite to fit and wrap extra filter

fabric around open core edge to prevent soil from entering core.

E.	At the top of the sheet drain installation, wrap the filter fabric flap behind the exposed top core edge to prevent intrusion of soil into the core and secure sheet drain to wall with termination bar fastened 12" (300 mm) on center.

3.07	INSULATION

A.	Always apply Volclay Panel waterproofing directly to properly prepared structural concrete substrates. Insulation, if used, should be applied over the waterproofing and drainage. Do not apply Volclay Panel waterproofing over lightweight insulating concrete.

- 3.08 	PROTECTION COURSE

- A.	Compactable soil backfill, free of debris and gravel does not require a protection course.  If backfill contains debris or gravel, then a protection course is required. Consult manufacturer when special conditions exist. Aquadrain prefabricated drainage composite may double function as a protection course. Do not use expanded polystyrene (bead board) as a protection course.

07170-7

3.09	BACKFILL EXCAVATED CAST-IN-PLACE CONCRETE WALLS

A.	Closely coordinate Volclay Panel installation with Backfill conducted under Division 31 work. Care should be used during backfill operation to avoid damage to the waterproofing system. Follow generally accepted practices for backfilling and compaction. Backfill should be added in 6" to 12" (150 - 300 mm) lifts and compacted to a minimum 85% Modified Proctor density. Protection course required with gravel backfill. Limit gravel backfill to <3/4” (18 mm) angular aggregate with fines.

3.10	CLEAN UP

- Clean areas where adjacent finished surfaces are soiled by work of this Section. Remove all tools, equipment and remaining product on-site. Dispose of section work debris and damaged product following all applicable regulations.

End of Section 071700