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Product Guide Specification
	Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, contained in the CSI Manual of Practice.
The section is a draft intended to expedite development of a final specification.  It must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the drawings.

Delete all “Specifier Notes” when editing this section.



SECTION 05530


METAL GRATINGS
	Specifier Notes:  This section covers metal gratings fastened to support steel with Hilti Powder Actuated X-FCM Grating Fastening System.  Consult Hilti for assistance in editing this section for the specific application.


PART 1
GENERAL
1.1
SECTION INCLUDES

A.
Metal gratings fastened to support steel with powder-actuated grating fastening system.

1.2
RELATED SECTIONS
	Specifier Notes:  Edit the following list of related sections as required for the project.  List other sections with work directly related to this section.


A.
Section 05120 - Structural Steel.

1.3
REFERENCES

	Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.


A.
ANSI A10.3 - Powder-Actuated Fastening Systems -- Safety Requirements.

B.
ANSI/NAAMM MBG 531 - Metal Bar Grating Manual.

C.
ASTM A 123 - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

D.
ASTM A 153 - Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

E.
ASTM A 510 - Standard Specification for General Requirements for Wire Rods and Coarse Round Wire, Carbon Steel.

F.
ASTM A 780 - Standard Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings.

G.
ASTM B 221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

H.
ISO 9001 - Quality Management Systems -- Requirements.

I.
ISO 14001 - Environmental Management Systems -- Specification with Guidance for Use.

1.4
SUBMITTALS

A.
Comply with Section 01330 - Submittal Procedures.

B.
Product Data:

1.
Submit grating manufacturer's product data, including load tables.

2.
Submit fastener manufacturer's product data, including installation instructions.

C.
Shop Drawings:  Submit grating manufacturer's shop drawings, indicating grating type, material, bearing bar size and spacing, cross bar spacing, top surface type, dimensions, tolerances, clearances, span, fabrication, shop welding, supports, toe plates, banding bars, cutouts, stair treads, finish, and location of fasteners.

D.
Samples:  Submit fastener manufacturer's samples of grating fasteners.

E.
Manufacturer's Certification:  Submit fastener manufacturer's certification indicating supplied grating fasteners comply with manufacturer’s published specifications.
1.5
QUALITY ASSURANCE
A. Grating Fastener Manufacturer:  ISO 9001 and ISO 14001 certified company.

B. Grating Fasteners:  Lloyd’s Registered and ABS Type Approved.

C.
Field Measurements:  Take field measurements before preparation of shop drawings and fabrication, as necessary.

1.6
DELIVERY, STORAGE, AND HANDLING
A.
Delivery:

1.
Gratings:  Deliver metal gratings to site with labels on each panel clearly identifying manufacturer, panel size, and location of installation.

2.
Fasteners:  Deliver grating fasteners to site in manufacturer's original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.
Storage:

1.
Gratings:  Store metal gratings flat, in clean, dry area, off ground in accordance with grating manufacturer's instructions.  Protect grating edges from damage.

2.
Fasteners:  Store grating fasteners in clean, dry area in accordance with fastener manufacturer's instructions.

C.
Handling:  Protect materials and finish from damage during handling and installation.

PART 2
PRODUCTS
2.1
MANUFACTURERS
A.
Metal Grating Manufacturers:

	Specifier Notes:  List acceptable metal grating manufacturers.


1.
____________________ .

2.
____________________ .

3.
____________________ .

B.
Grating Fastener Manufacturer:

1.
Hilti, Inc., PO Box 21148, Tulsa, Oklahoma 74121.  Toll Free (800) 879-8000.  Fax (800) 879-7000.  Technical Support (800) 879-6000 x6337.  Web Site www.us.hilti.com.

2.
Other manufacturers will not be allowed.

2.2
METAL GRATINGS

	Specifier Notes:  Consult manufacturer's catalogs when specifying the metal gratings.


A.
General:  Manufacturing, fabrication, welding, and tolerances shall be in accordance with  ANSI/NAAMM MBG 531.

	Specifier Notes:  Specify grating type.


B.
Type:  [Welded steel]  [Pressure-locked steel]  [Pressure-locked aluminum flush top]  [Pressure-locked aluminum rectangular bar]  [Pressure-locked aluminum I-Bar]  

[ ____________________ ].

C.
Material and Finish:

	Specifier Notes:  Specify grating material and finish.  Consult manufacturer's catalogs for finishes available.


1.
Steel:

a.
Bearing Bars:  ASTM A 36.

b.
Cross Bars:  ASTM A 510.

c.
Finish:  [Hot-dipped galvanized after fabrication, ASTM A 123]  [Painted, 1 coat manufacturer's standard red or black paint]  [ ____________________ ].

2.
Aluminum:

a.
Bearing Bars:  ASTM B 221, Alloy 6061-T6 or 6063-T6.

b.
Cross Bars:  ASTM B 221, Alloy 6061-T1.

c.
Finish:  [Mill]  [Class I clear anodized].

3.
Stainless Steel:

a.
Finish:  Mill.

D.
Bearing Bars:

	Specifier Notes:  Specify bearing bar size and spacing.  Hilti Powder Actuated X-FCM Grating Fastening System can accommodate a grating depth of 1 to 2 inches.  Consult Hilti if a grating depth greater than 2 inches is required.

The grating fastening system requires a minimum clear distance between bearing bars of 3/4 inch and a maximum bearing bar spacing of 1-3/16 inches on center.


1.
Depth:  [1 inch]  [1-1/4 inches]  [1-1/2 inches]  [1-3/4 inches]  [2 inches]  [ _____ inches]  [As indicated on the drawings].

2.
Thickness:  [1/8 inch]  [3/16 inch]  [ _____ inch]  [As indicated on the drawings].

3.
Spacing:  [1-3/16 inches on center]  [15/16 inches on center]  [ _____ inches on center]  [As indicated on the drawings].

	Specifier Notes:  Specify cross bar spacing.


E.
Cross Bar Spacing:  [4 inches on center]  [2 inches on center]  [ _____ inches on center]  [As indicated on the drawings].

	Specifier Notes:  Specify grating top surface.


F.
Top Surface:  [Plain]  [Serrated]  [Abrasive finish, aluminum oxide aggregate in epoxy resin adhesive]  [ ____________________ ]  [As indicated on the drawings].

G.
Toe Plates:

	Specifier Notes:  Specify toe plate height.


1.
Height:  [4 inches]  [ _____ inches]  [As indicated on the drawings].

	Specifier Notes:  Specify toe plate attachment.


2.
Attachment:  [Attach toe plates to gratings by welding in shop.]  [As indicated on the drawings.]

H.
Banding Bars:  Provide ends of grating panels and openings in gratings with banding bars of same material and height as gratings.

I.
Stair Treads:

1.
Same metal grating type, material, finish, bearing bars, and top surface.

	Specifier Notes:  Specify type of nosings.  Consult manufacturer's catalogs for nosings available.


2.
Nosings:  [Cast abrasive]  [Corrugated angle]  [ _______________ ]  [As indicated on the drawings].

2.3
GRATING FASTENERS
	Specifier Notes:  There are a number of methods to secure metal gratings to support steel.  Only the Hilti Powder Actuated X-FCM Grating Fastening System is specified in this section.  The X-FCM Grating Fastening System consists of two components:  an 8 mm threaded stud (either X-CRM8 and X-BT-RM8) and the X-FCM Grating Disk.  The X-CRM8 stud is AISI 316 equivalent for corrosive environment applications.  The X-BT-RM8 is AISI 316 equivalent for corrosive environment applications where the threaded stud fastener point must not penetrate the support steel.  The X-BT-RM8 is available with and without an AISI 316 washer with bonded black elastomeric sealing washer.  Consult Hilti for more information regarding these grating fastening systems.


A.
Fasteners:  Hilti Powder Actuated X-FCM Grating Fastening System.

1.
Grating Disks:  Assembly of 52 mm diameter disk and 8 mm internally threaded screw.

	Specifier Notes:  Specify grating disk material.


a.
Carbon Steel:  AISI 1008.  Hot-dip zinc galvanized, ASTM A 153 to a minimum of 65 micrometers thickness.

b.
Stainless Steel:  AISI 316 or equivalent.

2.
Threaded Studs:  8 mm powder-actuated threaded studs fastened to support steel in field with Hilti powder-actuated fastening tool equipped with grating adapter that fits through gratings and contacts support steel.

	Specifier Notes:  Specify Hilti X-CRM8 stainless steel threaded studs for hot-dip zinc galvanized carbon steel and stainless steel grating disks in corrosive environment applications.  Specify Hilti X-BT-RM8 stainless steel threaded studs for hot-dip galvanized carbon steel and stainless steel grating disks in corrosive environment applications where threaded stud fastener point must not penetrate through support steel.  Contact Hilti for more information on threaded studs.


a.
Stainless Steel:  AISI 316 or equivalent with Rockwell Hardness of 47 minimum.

PART 3
EXECUTION
3.1
EXAMINATION
A.
Examine support steel to receive metal gratings for correct size, layout, and alignment.  Notify Engineer if supports are not acceptable.  Do not begin installation until unacceptable conditions have been corrected.

3.2
INSTALLATION - METAL GRATINGS
A.
Install metal gratings in accordance with grating manufacturer's instructions and ANSI/NAAMM MBG 531 at locations indicated on the drawings.

B.
Ensure support steel bearing surfaces are clean.

C.
Install gratings level, square, rigid, with flush installation, and without warp.

D.
Install gratings with cross bars in alignment.

E.
Support grating panels on all sides and attach to support steel with a minimum of two fasteners per full-size panel width.  
F.
Cut openings for penetrations accurately to size and location.

G.
Cut openings for pipes a minimum of 2 inches larger in diameter than pipe.

	Specifier Notes:  Specify the following sentence for galvanized steel gratings.


H.
Repair damaged galvanized steel grating surfaces and apply galvanizing repair paint in accordance with ASTM A 780.

	Specifier Notes:  Specify the following sentence for aluminum gratings.


I.
Protect aluminum grating surfaces from direct contact with dissimilar metals by painting dissimilar metal with 1 coat of bituminous paint or other approved insulating material.

J.
Replace defective or damaged gratings as directed by Engineer.

3.3
INSTALLATION - GRATING FASTENERS
A.
Install grating fasteners to clamp grating to support steel in accordance with fastener manufacturer's instructions.

B.
Fasten threaded studs to support steel using fastening tools provided by fastener manufacturer.

C.
Operate powder-actuated fastening tools only with operators trained and qualified by fastener manufacturer's authorized instructor in accordance with ANSI A10.3.

D.    Drive threaded studs into support steel to proper embedment depth in accordance with fastener 

         manufacturer's instructions.

	Specifier Notes:  X-BT-RM8 threaded studs must be installed into pre-drilled holes (4 mm diameter by 3/16 inch deep) in the support steel. Contact Hilti for X-BT-RM8 installation instructions.


E.
Fasten threaded studs perpendicular to support steel.

F.
Use proper grating disk length to accommodate grating depth.

G.
Tighten internally threaded screw of grating disk onto threaded stud with maximum tightening torque depending on thickness of support steel in accordance with fastener manufacturer's instructions.  Use tightening tool provided by fastener manufacturer.

H.
Install fasteners with a minimum thread engagement of 5 mm between grating disk internally threaded screw and threaded stud.

3.4
FIELD QUALITY CONTROL
A.
Fastener Manufacturer's Field Services:  Fastener manufacturer's authorized instructor shall train and qualify operators for manufacturer's powder-actuated fastening tools in accordance with ANSI A10.3.

3.5
PROTECTION
A.
Protect installed metal gratings and fasteners from damage during construction.


END OF SECTION
Metal Gratings
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