Copyright 2019 by The American Institute of Architects (AIA)

This Product MasterSpec Section is licensed by Deltek, Inc. to Activar Construction Products Group, Inc. - JL Industries ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Activar Construction Products Group, Inc. - JL Industries, 9702 Newton Ave. S., Bloomington, MN 55431; Phone (800) 554-6077; Website: www.activarcpg.com; Email: sales@activarcpg.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 083113 - ACCESS DOORS AND FRAMES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Access doors and frames.

          - Fire-rated access doors and frames.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 077200 "Roof Accessories" for roof hatches.

          - Section 083113.53 "Security Access Doors and Frames" for access doors and frames for security applications.

          - Section 083483 "Floor Doors" for doors installed in floors.

          - Section 233300 "Air Duct Accessories" for heating and air-conditioning duct access doors.

      - ALLOWANCES

Retain products and Work included in this Section that are covered by cash or quantity allowance. Do not include amounts. Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the allowance.

        - Access doors and frames are part of an access door and frame allowance.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

Retain option in subparagraph below if fire-rated units are included in the Work.

          - Include construction details[, fire ratings,] material descriptions, dimensions of individual components and profiles, and finishes.

        - Samples: For each type of access door and frame and for each finish specified, complete assembly minimum 6 by 6 inches (150 by 150 mm) in size.

        - Product Schedule: For access doors and frames.[ Use same designations indicated on Drawings.]

        - Sustainable Design Submittals:

Retain "Product Data" Subparagraph below to require minimum recycled content for LEED 2009 MR Credit 4 - "Recycled Content."

          - Product Data: For recycled content, indicating postconsumer and preconsumer recycled content and cost.

          - Environmental product declaration.

"Product Certificates" Subparagraph below applies to LEED 2009, Materials and Resources Credit 5, "Regional Materials."

          - Product Certificates: For regional materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project and cost for each regional material.

Retain "Environmental Product Declaration (EPD)" Subparagraph below for LEED v4 "MRc Building Product Disclosure and Optimization - Environmental Product Declarations." See the Evaluations. Verify, with manufacturer, that EPDs are available for each product.

          - Environmental Product Declaration (EPD): For each product.

"Product Certificates" Subparagraph below applies to IgCC, which requires that a minimum of 55 percent of building materials or products be extracted, harvested, manufactured, or recovered within 500 miles (800 km) of Project. See IgCC-2012, 505.2.5.

          - Product Certificates: For indigenous materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project, means of transportation, and cost for each indigenous material.

Retain "Environmental Product Declaration" Subparagraph below if products specified in the Section are required to have an EPD to meet the IgCC's requirement of 55 percent recycled materials.

          - Environmental Product Declaration: For each product.

"Product Certificates" Subparagraph below applies to ASHRAE 189.1, which requires that a minimum of 15 percent of building materials or products be extracted, harvested, manufactured, or recovered within 500 miles (800 km) of Project. See ASHRAE 189.1-2014, 9.4.1.2.

          - Product Certificates: For regional materials, indicating location of material manufacturer and point of extraction, harvest, or recovery for each raw material. Include distance to Project, means of transportation, and cost for each regional material.

"Environmental Product Declaration" Subparagraph below applies to ASHRAE 189.1 if products specified in the Section are used to meet the requirements of paragraph 9.4.1.4, "Multiple-Attribute Product Declaration or Certification," which requires EPDs for a minimum of 10 products.

          - Environmental Product Declaration: For each product.

Subparagraphs below apply to Green Globes v1.4  if products specified in the Section are used to meet the requirements of paragraph 3.5.1.2 "Path B: Prescriptive Path for Building Core and Shell" -which requires that a certain percentage of the materials used in the core and shell have EPDs, third-party certifications, and/or third-party life cycle assessments.

          - Environmental Product Declaration: For each product.

          - Third-Party Certifications: For each product.

          - Third-Party Certified Life Cycle Assessment: For each product.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For testing and inspecting agency.

Retain "Fire-Rated Door Inspector" Subparagraph below, or delete and retain second subparagraph below. Certification in second subparagraph below should be acceptable by all authorities having jurisdiction. See the Evaluations.

          - Fire-Rated Door Inspector: Submit documentation of compliance with NFPA 80, Section 5.2.3.1.

          - Submit copy of DHI Fire and Egress Door Assembly Inspector (FDAI) certificate.

Coordination drawings, as an informational submittal, may be added if required for complex projects or for spaces where the layout of access doors and frames on ceilings is important to the design.

      - CLOSEOUT SUBMITTALS

        - Record Documents: For fire-rated doors, list of applicable room name and number in which access door is located.

      - QUALITY ASSURANCE

        - Fire-Rated Door Inspector Qualifications: Inspector for field quality control inspections of fire-rated door assemblies shall meet the qualifications set forth in NFPA 80, Section 5.2.3.1 and the following:

Retain subparagraph below if requiring fire door inspectors to be certified under DHI's certification program. Verify, with authorities having jurisdiction, if other DHI certifications are acceptable, such as Architectural Hardware Consultant (AHC), Certified Door Consultant (CDC), and Architectural Openings Consultant (AOC).

          - Door and Hardware Institute Fire and Egress Door Assembly Inspector (FDAI) certification.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

Retain this article if fire-rated units are required. Retain option if temperature-rise assemblies are required.

        - Fire-Rated Access Doors and Frames: Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency, for fire-protection[ and temperature-rise limit] ratings indicated, in accordance with NFPA 252 or UL 10B.

      - MANUFACTURERS

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; Basis-of-Design product indicated or comparable product by one of the following:

          - Acudor Products Inc.

          - Cendrex Inc.

          - Karp Associates, Inc.

          - <Insert manufacturer's name>.

      - ACCESS DOORS AND FRAMES

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Flush Access Doors with Exposed Flanges <Insert drawing designation>:

- TM: Multipurpose Galvanized Steel Flush Access Door, Concealed Hinge with Exposed Flange.

- TMG: Multipurpose Galvannealed Steel Flush Access Door, Concealed Hinge with Exposed Flange.

- TMS: Multipurpose Stainless Steel Flush Access Door, Concealed Hinge with Exposed Flange.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [TM] [TMG] [TMS] or comparable product.

          - Description: Face of door flush with frame, with exposed 1 inch (25 mm) flange and[ 90-degree] continuous concealed hinge.

Revise "Optional Features" Subparagraph below to suit project.

          - Optional Features: [Four-sided gasketing] [Piano hinges] [Double-leaf doors] [Louvers] [Inward swing] [Rain hood] [Masonry anchors] [Removable doors] [View window] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Flange Width: 1 inch (25.4 mm).

First option in "Door Size" Subparagraph below available with JL Industries "TM" or "TMS" access door models.

          - Door Size: [6 by 6 inches (152 by 152 mm)] [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [24 by 36 inches (609 by 914 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door," "Powder-Coated Galvannealed Steel Sheet for Door" or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: [Nominal 0.062 inch (1.59 mm), 16 gage] [Nominal 0.050 inch (1.27 mm), 18 gage] <Insert thickness>, ASTM A480/A480M No. 4 finish.

Retain first option in "Frame Material" Subparagraph before for "TM" or "TMG" models; retain second option for "TMS" models.

          - Frame Material: [Same material, thickness, and finish as door] [Nominal 0.050 inch (1.27 mm), 18 gage] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

Retain first option in "Latch and Lock" Paragraph below for JL Industries standard latch.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, torx-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Cylinder] [Prepared for 1-1/8 inch (28.57 mm) diameter lock with 1-1/4 inch (31.75 mm) length mortise cylinder] [Mortise deadbolt] [Mortise slam latch] [As indicated on Drawings] [As indicated in schedule] [ with interior release].

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Flush Access Doors with Concealed Flanges for Wallboard <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

Select from models "TMW," "TMWG" and "TMWS" for concealed frame flush panels with wallboard flange that can be taped and mudded to achieve a concealed look on walls or ceilings.

- TMW: Galvanized Steel Flush Access Door, Concealed Hinge with Wallboard Bead Flange.

- TMWG: Galvannealed Steel Flush Access Door, Concealed Hinge with Wallboard Bead Flange.

- TMWS: Stainless Steel Flush Access Door, Concealed Hinge with Wallboard Bead Flange

Retain "Basis-of-Design Product" Paragraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [TMW] [TMWG] [TMWS] or comparable product.

          - Description: Face of door flush with frame; with concealed flange for gypsum board installation and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable doors] [View window] [Inward swing] [Rain hood] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

Revise "Door Size" Subparagraph below to suit project. Consult manufacturers for availability.

Maximum "door size" option below for walls is 36 by 48 inches; ceiling maximum is 36 by 36 inches.

          - Door Size: [6 by 6 inches (152 by 152 mm)] [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [36 by 48 inches (914 by 1219 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door," "Powder-Coated Galvannealed Steel Sheet for Door" or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

Retain "Stainless Steel Sheet for Door" Subparagraph with JL Industries "TMWS" models.

          - Stainless Steel Sheet for Door: [Nominal 0.078 inch (1.98 mm), 14 gage] [Nominal 0.062 inch (1.59 mm), 16 gage], ASTM A480/A480M No. 4 finish.

          - Frame Material: [Same material and thickness as door] [Nominal 0.078 inch (1.98 mm), 14 gage] [Nominal 0.062 inch (1.59 mm), 16 gage].

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

Retain first option in "Latch and Lock" Paragraph below for JL Industries standard.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

        - Flush Access Doors with Concealed Flanges for Plaster <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

Select from models "TME," "TMEG," TMES, "TMP," "TMPG," and "TMPS" for concealed frame flush panels with recessed flanges for plaster application.

- TME: Galvanized Steel Flush Access Door, Concealed Hinge with Recessed Flange.

- TMEG: Galvannealed Steel Flush Access Door, Concealed Hinge with Recessed Flange.

- TMES: Stainless Steel Flush Access Door, Concealed Hinge with Recessed Flange.

- TMP: Galvanized Steel Flush Access Door, Concealed Hinge with Extended Width Recessed Flange.

- TMPG: Galvannealed Steel Flush Access Door, Concealed Hinge with Extended Width Recessed Flange.

- TMPS: Stainless Steel Flush Access Door, Concealed Hinge with Extended Width Recessed Flange.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [TME] [TMEG] [TMES] [TMP] [TMPG] [TMPS] <Insert product name or designation> or comparable product.

          - Description: Face of door flush with frame with concealed flange for plaster installation and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable doors [View window] [Inward swing] [Rain hood] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

Retain first option in "Flange" Subparagraph below for JL Industries standard width recessed plaster flange; retain second option for extended width recessed steel lath.

          - Concealed Flange Width: [1-3/8-inch (34.92 mm)] [2-3/4-inch (69.85 mm)].

Revise "Door Size" Subparagraph below to suit project. Consult manufacturers for availability.

Maximum "door size" option below for walls is 36 by 48 inches; ceiling maximum is 36 by 36 inches.

          - Door Size: [6 by 6 inches (152 by 152 mm)] [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [36 by 48 inches (914 by 1219 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door," "Powder-Coated Galvannealed Steel Sheet for Door" or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: Nominal 0.062 inch (1.59 mm), 16 gage, ASTM A480/A480M No. 4 finish.

          - Frame Material: Same material and thickness as door.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

Retain first option in "Latch and Lock" Paragraph below for JL Industries standard.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

        - Recessed Access Doors with Exposed Flanges <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ACUDOR Products, Inc.

            - Cendrex Inc.

            - Karp Associates, Inc.

            - <Insert manufacturer's name>.

          - Description: Door face recessed [1/2 inch (13 mm)] [5/8 inch (16 mm)] [1 inch (25mm)] for [gypsum board] [plaster] [acoustical tile] <Insert material> infill, with exposed flange and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable doors] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: <Insert door size>.

Retain "Uncoated Steel Sheet for Door," "Metallic-Coated Steel Sheet for Door," or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

          - Uncoated Steel Sheet for Door: [Nominal 0.060 inch (1.52 mm), 16 gage] <Insert thickness>, factory [primed] [finished].

          - Metallic-Coated Steel Sheet for Door: [Nominal 0.064 inch (1.63 mm), 16 gage] <Insert thickness>, factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: [Nominal 0.062 inch (1.59 mm), 16 gage] <Insert thickness>, ASTM A480/A480M No. 4 finish.

          - Frame Material: [Same material and thickness as door] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Recessed Access Doors with Concealed Flanges<Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

JL Industries "CT Series" recessed concealed frame access doors feature heavy construction.

- CT: Galvanized Steel Recessed Access Door with Trimless Frame.

- CTG: Galvannealed Steel Recessed Access Door with Trimless Frame.

- CTE: Galvanized Steel Recessed Access Door with Recessed Frame with Metal Lath Flange for Plaster.

- CTEG: Galvannealed Steel Recessed Access Door with Recessed Frame with Metal Lath Flange for Plaster.

- CTW: Galvanized Steel Recessed Access Door with Recessed Frame with Drywall Bead Flange.

- CTWG: Galvannealed Steel Recessed Access Door with Recessed Frame with Drywall Bead Flange.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [CT] [CTG] [CTE] [CTEG] [CTW] [CTWG] or comparable product.

Revise "Description" Subparagraph below to include optional features or construction such as gasketing, double-leaf doors, piano hinges, louvers, masonry anchors, and removable doors. Consult manufacturers for availability.

Retain first face-depth option in "Description" Subparagraph below with JL Industries "CT," "CTG," "CTW," or "CTWG" access doors; retain second face-depth option with "CTE" or "CTEG" access doors.

          - Description: Door face recessed [1/2 inch (13 mm)] [5/8 inch (16 mm)] for [gypsum board] [plaster] [acoustical tile] <Insert material> infill; with concealed flange for [gypsum board] [plaster] [no bead for acoustical tile] installation and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable door] [View window] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door," "Powder-Coated Galvannealed Steel Sheet for Door," or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

          - Stainless Steel Sheet for Door: [Nominal 0.062 inch (1.59 mm), 16 gage] <Insert thickness>, [ASTM A480/A480M No. 4] [ASTM A480/A480M No. 2b] finish.

          - Frame Material: [Same material and thickness as door] [Nominal 0.078 inch (1.98 mm), 14 gage] [Nominal 0.062 inch (1.59 mm), 16 gage].

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

Retain first option in "Latch and Lock" Paragraph below for JL Industries standard latch.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Aluminum Flush Access Doors <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Lane-Aire Manufacturing Corp.

            - MIFAB, Inc.

            - Williams Bros. Corporation of America (The).

            - <Insert manufacturer's name>.

          - Description: Face of door flush with frame, with exposed flange and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable doors] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: <Insert door size>.

          - Aluminum Sheet for Door: [Nominal 0.045 inch (1.15 mm)] <Insert thickness>, with [mill] [manufacturer's standard baked-enamel or powder-coat] finish.

          - Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Lightweight Flush Access Doors <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Acudor Products Inc.

            - Cendrex Inc.

            - Karp Associates, Inc.

            - <Insert manufacturer's name>.

          - Description: Face of door flush with exposed flange, with exposed piano hinge; frameless for surface installation.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Gasketing] [Double-leaf doors] [Piano hinges] [Louvers] [Masonry anchors] [Removable door] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: <Insert door size>.

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project. Confirm material thicknesses, which vary widely by manufacturer. Confirm frame material; some manufacturers provide aluminum frames.

          - Uncoated Steel Sheet for Door: [Nominal 0.018 inch (0.46 mm), 26 gage] <Insert thickness>, factory [primed] [finished].

          - Metallic-Coated Steel Sheet for Door: [Nominal 0.022 inch (0.56 mm), 26 gage] <Insert thickness>, factory [primed] [finished].

          - Frame Material: [Aluminum, nominal 0.045 inch (1.15 mm), mill finish] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Latch bolt, key operated] [Prepared for mortise cylinder] [As indicated on Drawings] [As indicated in schedule] <Insert operator>[ with interior release].

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Exterior Flush Access Doors <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

- XTA: Aluminum Flush Insulated Access Door with Galvannealed Steel Frame.

- XTS: Stainless Steel Flush Insulated Access Door and Frame.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [XTA] [XTS] or comparable product.

          - Description: Weatherproof assembly, with face of door fit flush with frame and with exposed frame. Include extruded door gaskets and minimum 2-inch- (50-mm-) thick polyisocyanurate insulation.

Revise "Optional Features" Subparagraph below to include optional features or construction.

          - Optional Features: [Rainhood] <Insert feature>.

          - Locations: [Wall] <Insert location or substrate>.

          - Flange Width: 1 inch (25.4 mm).

          - Door Size: [8 by 8 inches (203 by 203 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 24 inches (508 by 609 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [24 by 36 inches (609 by 914 mm)] [24 by 48 inches (609 by 1219 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [48 by 48 inches (1219 by 1219 mm)].

Retain "Aluminum Sheet for Door," with JL Industries "XTA" model insulated access door; or "Stainless Steel Sheet for Door" with "XTS" model. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

          - Aluminum Sheet for Door: [Nominal 0.040 inch (1.01 mm)] <Insert thickness>, with  manufacturer's standard baked-enamel or powder-coat finish.

          - Stainless Steel Sheet for Door: [Nominal 0.062 inch (1.59 mm), 16 gage] [Nominal 0.040 inch (1.01 mm), 20 gage] <Insert thickness>, [ASTM A480/A480M No. 4] [ASTM A480/A480M No. 2b] finish.

          - Frame Material: [Same material, thickness, and finish as door] [Nominal 0.064 inch (1.63 mm), 16 gage].

          - Latch and Lock: Cam latch operated by handle, [without lock] [with keyed lock in handle] [with separate mortise lock] [with preparation for mortise lock] [as indicated on Drawings] [as indicated in schedule] <Insert operator>[; with interior release].

          - Gasketing: Adhesive based EPDM foam and silicone rubber gasket around perimeter of door frame and panel.

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Interior Specialty Access Doors, Gasketed <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

JL Industries models "AT," "ATG" and "ATS" gasketed access panels are ideal for laboratories, pressurized rooms, climate-controlled rooms, and dusty or high-moisture environments.

- AT: Steel Access Door with Cold-Rolled Steel Frame, Fully-Gasketed.

- ATG: Galvannealed Steel Access Door and Frame, Fully Gasketed.

- ATS: Stainless Steel Access Door and Frame, Fully Gasketed.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [AT] [ATG] [ATS] or comparable product.

          - Description: Fully gasketed door panel with flanged frame and continuous hinge.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Flange Width: 1-1/4-inch (31.75 mm).

          - Door Size: [12 by 12 inches (304 by 304 mm)] [18 by 18 inches (457 by 457 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 36 inches (609 by 914 mm)].

Retain "Powder-Coated Cold-Rolled Steel Sheet for Door," "Powder-Coated Galvannealed Steel Sheet for Door" or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain option in "Powder-Coated Cold-Rolled Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Cold-Rolled Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain option in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: [Nominal 0.078 inch (1.98 mm), 14 gage] [Nominal 0.062 inch (1.59 mm), 16 gage], ASTM A480/A480M No. 4 finish.

          - Frame Material: [Same material and thickness as door] [Nominal 0.078 inch (1.98 mm), 14 gage] [Nominal 0.062 inch (1.59 mm), 16 gage].

          - Latch and Lock: [Knurled-knob, cam latch] [Flush handle] [Locking flush handle].

          - Gasketing: Full, four-sided EPDM rubber gasketing.

Copy paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Interior Specialty Access Doors, Surface-Mountable <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

- SM: Surface-Mountable Steel Access Door with Trim.

- SMS: Surface-Mountable Stainless Steel Access Door with Trim.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [SM] [SMS] or comparable product.

          - Description: Surface-mountable continuous hinge door panel and 1 inch (25.4 mm) trim with corner screw holes for surface attachment.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: [8 by 8 inches (203 by 203 mm)] [12 by 12 inches (304 by 304 mm)] [16 by 16 inches (406 by 406 mm)] [24 by 24 inches (609 by 609 mm)] [36 by 36 inches (914 by 914 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door" or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: Nominal 0.064-inch (1.63-mm), 16 gage, cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: Nominal 0.062 inch (1.59 mm), 16 gage, ASTM A480/A480M No. 4 finish.

          - Frame Material: [Same material and thickness as door].

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [As indicated on Drawings] [As indicated in schedule] <Insert operator>.

        - Interior Sound Rated Access Doors <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

- STCS: Surface-Mountable Sound Rated, Stainless Steel Access Door with Trim.

- STCG: Surface-Mountable Sound Rated, Galvannealed Steel Access Door with Trim.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [STCS] [STCG] or comparable product.

          - Description: Sound rated, continuous hinge door panel and 1 inch (25.4 mm).

          - Locations: Wall .

          - Door Size: [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [24 by 36 inches (609 by 914 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door" or " Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: Nominal 0.064-inch (1.63-mm), 16 gage, cold-rolled steel [with structural side-fold reinforcing], factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: [Nominal 0.078-inch (1.98-mm), 14 gage] [Nominal 0.064-inch (1.63-mm), 16 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: Nominal 0.062 inch (1.59 mm), 16 gage, ASTM A480/A480M No. 4 finish.

          - Frame Material: Nominal 0.038 inch (0.95 mm), 20 gage.

Retain first option in "Latch and Lock" Subparagraph below for JL Industries standard lock.

          - Latch and Lock: [Non-locking compression paddle latch] [Manufacturer's standard for door size and type].

          - Sound Rating: 47.

        - Interior Flush GFRG Access Doors <Insert drawing designation>:

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product information.

- GF: Square Drop-in Ceiling Panel with Square or Radius Corner.

- GFH: Wall or Ceiling Panel with Hinges and Cam Latch and Square or Radius Corner.

- GFR: Round Drop-in Ceiling Panel.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [GF] [GFH] [GFR] or comparable product.

          - Description: Face of [drop-in] [concealed-hinge] door flush with frame, with concealed flange for gypsum board installation.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: [9 by 9 inches (228 by 228 mm)] [12 by 12 inches (304 by 304 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [24 by 24 inches (609 by 609 mm)] [30 by 30 inches (762 by 762 mm)].

          - Door Type [Drop in, radius corner] [Drop in, square corner] [Concealed-hinge, radius corner] [Concealed-hinge, square corner].

          - Door and Frame Material: Unpainted glass-fiber-reinforced gypsum, with frames reinforced for hardware and fastenings.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [As indicated on Drawings] [As indicated in schedule] <Insert operator>.

        - Exterior Flush GFRC Access Doors with Concealed Flanges <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Acudor Products Inc.

            - Cendrex Inc.

            - Karp Associates, Inc.

            - <Insert manufacturer's name>.

          - Description: Face of door flush with frame, neoprene gasketed, with concealed flange for gypsum board installation.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Piano hinges] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

          - Door Size: <Insert door size>.

          - Door Type: [Drop in, radius corner] [Drop in, square corner] [Concealed-hinge, radius corner] [Concealed-hinge, square corner].

          - Door and Frame Material: Unpainted glass-fiber-reinforced cement, with frames reinforced for hardware and fastenings.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Cam latch, hex-head wrench operated] [Cam latch, pinned-hex-head wrench operated] [As indicated on Drawings] [As indicated in schedule] <Insert operator>.

      - FIRE-RATED ACCESS DOORS AND FRAMES

Copy first paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Fire-Rated, Heavy-Duty Flush Access Doors with Exposed Flanges <Insert drawing designation>:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; FD-Heavy Gage or comparable product.

All JL Industries fire rated access doors are insulated.

          - Description: Heavy-duty door face flush with frame, with a core of mineral-fiber insulation enclosed in sheet metal, and masonry anchors; with exposed flange, self-closing door, and continuous hinge.

          - Locations: Wall.

          - Flange Width: 1 inch (25.4 mm).

          - Door Size: [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [48 by 48 inches (1219 by 1219 mm)].

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [1 hour] [1-1/2 hours] [2 hours].

Retain "Powder-Coated Steel for Door," or "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain option in "Powder-Coated Steel for Door" Subparagraph below to suit Project.

          - Powder-Coated Steel for Door: Nominal 0.078-inch (1.98-mm), 14 gage, cold-rolled steel, factory [primed] [finished].

Retain option in "Powder-Coated Galvannealed Steel for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel for Door: Nominal 0.078-inch (1.98-mm), 14 gage, cold-rolled steel, factory [primed] [finished].

          - Frame Material: [Same material, thickness, and finish as door] [Nominal 0.038 inch (0.95 mm), 20 gage].

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices. The IBC requires rated doors to be self-closing and self-latching.

          - Latch and Lock: Self-latching door hardware, [operated by knurled-knob] [operated by key] [prepared for mortise cylinder] [as indicated on Drawings] [as indicated in schedule] <Insert operator>[ with interior release].

Copy paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Fire-Rated, Flush Access Doors with Exposed Flanges <Insert drawing designation>:

- FD: Fire-Rated Steel Access Door and Frame.

- FDG: Fire-Rated Galvannealed Steel Access Door and Frame.

- FDS: Fire-Rated Stainless Steel Access Door and Frame.

- FDCI: Fire-Rated Steel Upward Opening Access Door and Frame.

- FDWI: Fire-Rated Inward Swing Access Door and Frame.

- FD2D: Fire-Rated Insulated Double Door Access Door and Frame.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [FD] [FDG] [FDS] [FD2CI] [FD2WI] [FD2D] Series or comparable product.

All JL Industries fire-rated access doors are insulated.

          - Description: Door face flush with frame, with a core of mineral-fiber insulation enclosed in sheet metal; with exposed flange, self-closing door, and concealed hinge.

          - Optional Features: [Upward-opening doors for ceilings] [Inward-opening doors for ceilings] [Gasketing] [Double-leaf doors] [Masonry anchors] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling].

Retain first option in "Flange Width" Subparagraph below with JL Industries "FD2WI" or "FD2CI" access door models; retain second option with "FD" or "FDG" models.

          - Flange Width: [7/8-inch (22.2 mm)] [1 inch (25.4 mm)].

JL Industries "FD2CI" model available in 12 by 12 inches (304 by 304 mm) size. Consult manufacturer for availability.

          - Door Size: [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [48 by 48 inches (1219 by 1219 mm)].

JL Industries "FDCI" upward opening access door available with 2-, 3- or 4-hour rating.

JL Industries "FDWI" inward swing access door for wall available with 2-hour rating.

JL Industries "FD," "FDG," and "FDS" access doors available with 1- or 2-hour rating.

          - Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [1 hour] [1-1/2 hours] [2 hours] [3 hours] [4 hours].

Retain "Temperature-Rise Rating" Subparagraph below if required; verify availability with manufacturer.

          - Temperature-Rise Rating: [450 deg F (250 deg C)] [250 deg F (139 deg C)] at the end of 30 minutes.

Retain "Powder-Coated Steel for Door," or "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain first option in "Powder-Coated Steel for Door" for JL Industries standard material for rated access doors.

          - Powder-Coated Steel for Door: Nominal 0.036 inch (0.91 mm), 20 gage, factory [primed] [finished].

Retain options in "Powder-Coated Galvannealed Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvannealed Steel Sheet for Door: Nominal 0.040 inch (1.02 mm), 20 gage, factory [primed] [finished].

          - Frame Material: Nominal 0.064 inch (1.63 mm), 16 gage.

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: Nominal 0.038 inch (0.95 mm), 20 gage, ASTM A480/A480M No. 4 finish.

          - Frame Material: Same material, thickness, and finish as door.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices. The IBC requires rated doors to be self-closing and self-latching.

          - Latch and Lock: Self-latching door hardware, [operated by knurled-knob] [operated by key] [prepared for mortise cylinder] [as indicated on Drawings] [as indicated in schedule] <Insert operator>[ with interior release].

Copy paragraph below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Fire-Rated, Access Doors with Concealed Flanges <Insert drawing designation>:

- FDP: Fire-Rated Insulated Galvanized Access Door with Concealed Flange for Plaster.

- FDPS: Fire-Rated Insulated Stainless Steel Access Door with Concealed Flange for Plaster.

- FDW: Fire-Rated Insulated Galvanized Access Door with Concealed Drywall Bead Flange.

- FDWS: Fire-Rated Insulated Stainless Steel Access Door with Concealed Drywall Bead Flange.

- FD2RF: Fire-Rated Galvanized Steel Access Door with Recessed Flange for Trimless Appearance.

- FD2RFS: Fire-Rated Stainless Steel Access Door with Recessed Flange for Trimless Appearance.

- FD2D: Fire-Rated Insulated Double Door Access Door and Frame.

- FD2CT: Fire-Rated Galvanized Steel Recessed Access Door with Recessed Flange.

- FD2CTS: Fire-Rated Stainless Steel Recessed Access Door with Recessed Flange.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [FDP] [FDPS] [FDW] [FDWS] [FD2RF] [FD2RFS] [FD2D] [FD2CT] [FD2CTS] or comparable product.

All JL Industries fire-rated access doors are insulated.

Retain first option in "Description" Paragraph below with JL Industries fire rated access doors.

          - Description: Door face flush with frame, [with a core of mineral-fiber insulation enclosed in sheet metal] [uninsulated]; with concealed flange for [gypsum board] [plaster] installation, self-closing door, and concealed hinge.

Revise "Optional Features" Subparagraph below to include optional features or construction. Consult manufacturers for availability.

          - Optional Features: [Upward-opening doors for ceilings] [Gasketing] [Double-leaf doors] [Masonry anchors] <Insert feature>.

          - Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

48 by 60 inch size in "Door Size" Paragraph below is JL Industries maximum dimension for wall access doors models in "Basis-of-Design" Subparagraph above.

          - Door Size: [8 by 8 inches (203 by 203 mm)] [10 by 10 inches (254 by 254 mm)] [12 by 12 inches (304 by 304 mm)] [14 by 14 inches (355 by 355 mm)] [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 30 inches (508 by 762 mm)] [22 by 22 inches (558 by 558 mm)] [22 by 30 inches (558 by 762 mm)] [22 by 36 inches (558 by 914 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 30 inches (609 by 762 mm)] [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (914 by 914 mm)] [48 by 48 inches (1219 by 1219 mm)] [48 by 60 inches (1219 by 1524 mm)].

          - Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [45 minutes] [1 hour] [1-1/2 hours] [2 hours] [3 hours] <Insert requirement>.

Retain "Temperature-Rise Rating" Subparagraph below if required; verify availability with manufacturer.

          - Temperature-Rise Rating: [450 deg F (250 deg C)] [250 deg F (139 deg C)] at the end of 30 minutes.

Retain "Uncoated Steel Sheet for Door," "Metallic-Coated Steel Sheet for Door," or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project. Uninsulated access doors require thicker steel sheet.

          - Uncoated Steel Sheet for Door: [Nominal 0.036 inch (0.91 mm), 20 gage] <Insert thickness>, factory [primed] [finished].

          - Metallic-Coated Steel Sheet for Door: [Nominal 0.040 inch (1.02 mm), 20 gage] <Insert thickness>, factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: [Nominal 0.038 inch (0.95 mm), 20 gage] <Insert thickness>, ASTM A480/A480M No. 4 finish.

          - Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices. The IBC requires rated doors to be self-closing and self-latching.

          - Latch and Lock: Self-closing, self-latching door hardware, [operated by knurled-knob] [operated by key] [prepared for mortise cylinder] [as indicated on Drawings] [as indicated in schedule] <Insert operator>[, with interior release].

        - Fire-Rated, Oversized Flush Access Doors with Exposed Flanges <Insert drawing designation>:

- FD2: Fire-Rated Oversized Galvanized Steel Oversized Flush Access Door with Exposed Flange.

- FD2S: Fire-Rated Oversized Stainless Steel Flush Access Door with Exposed Flange.

- FD2LS: Fire-Rated Galvanized Steel Laundry or Garbage Chute Access Door with Exposed Flange.

- FD2LS: Fire-Rated Stainless Steel Laundry or Garbage Chute Access Door with Exposed Flange.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Activar Construction Products Group, Inc. - JL Industries; [FD2] [FD2LS] [FD2S] or comparable product.

All JL Industries fire rated access doors are insulated.

          - Description: Face of door flush with frame, with exposed 1-inch (25-mm) flange and[ 90-degree] continuous concealed hinge.

Revise "Optional Features" Subparagraph below to suit project.

          - Optional Features: [Four-sided gasketing] [Piano hinges] [Double-leaf doors] [Louvers] [Inward swing] [Rain hood] [Masonry anchors] [View window] <Insert feature>.

          - Locations: Wall.

Retain first option in "Flange Width" Subparagraph below with door sizes up to and including 36 by 36-inch; retain second option for larger sizes; retain third option with laundry/garbage chute model.

          - Flange Width: [7/8-inch (25.4 mm)] [1-1/4-inch (31.75 mm)] [1-3/4-inch (44.45 mm)].

JL Industries oversized fire-rated doors available in sizes up to 60 by 60-inch for wall doors or 36 by 36-inch for ceiling access doors. Verify size availability with manufacturer.

Visit http://www.activarcpg.com/jl-industries/access-panels for additional product and size information.

- FD2: Available in sizes ranging from 24 by 48 inch up to 48 by 60 inch.

- FD2L: Available in sizes ranging from 16 by 16 inch up to 30 by 30 inch.

          - Door Size: [16 by 16 inches (406 by 406 mm)] [18 by 18 inches (457 by 457 mm)] [20 by 20 inches (508 by 508 mm)] [22 by 22 inches (558 by 558 mm)] [24 by 24 inches (609 by 609 mm)] [24 by 48 inches (609 by 1219 mm)] [30 by 30 inches (762 by 762 mm)] [30 by 36 inches (762 by 914 mm)] [30 by 48 inches (762 by 1219 mm)] [32 by 32 inches (813 by 813 mm)] [36 by 36 inches (914 by 914 mm)] [36 by 60 inches (914 by 1524 mm)] [40 by 60 inches (1016 by 1524 mm)] [48 by 48 inches (1219 by 1219 mm)] [48 by 60 inches (1219 by 1524 mm)].

Retain "Powder-Coated Galvanized Steel Sheet for Door," or "Stainless Steel Sheet for Door" Subparagraph below. Because gage thickness is not defined by industry standards, decimal thickness must be indicated. Thicknesses shown are examples only; revise to suit Project.

Retain options in "Powder-Coated Galvanized Steel Sheet for Door" Subparagraph below to suit Project.

          - Powder-Coated Galvanized Steel Sheet for Door: [Nominal 0.050-inch (1.27-mm), 18 gage], cold-rolled steel[ with structural side-fold reinforcing], factory [primed] [finished].

Revise "Stainless Steel Sheet for Door" Subparagraph below for other finishes; ASTM A480/A480M No. 4 is typical.

          - Stainless Steel Sheet for Door: [Nominal 0.050 inch (1.27 mm), 18 gage] <Insert thickness>, ASTM A480/A480M No. 4 finish.

          - Frame Material: [Nominal 0.053 inch (1.61 mm), 16 gage] <Insert material, thickness, and finish>.

Revise "Latch and Lock" Subparagraph below for other hardware offered by some manufacturers; options include commonly available choices.

Retain first option in "Latch and Lock" Subparagraph below for JL Industries standard latch; retain third option with laundry/garbage chute model.

          - Latch and Lock: [Cam latch, screwdriver operated] [Cam latch, key operated] [Non-locking T-Handle] [Cam latch, hex-head wrench operated] [Cam latch, torx-head wrench operated] [Cam latch, spanner-head wrench operated] [Latch bolt, knurled-knob operated] [Cylinder] [Prepared for 1-1/8 inch (28.57 mm) diameter lock with 1-1/4 inch (31.75 mm) length mortise cylinder] [Mortise deadbolt] [Mortise slam latch] [As indicated on Drawings] [As indicated in schedule][ with interior release].

      - MATERIALS

Retain materials in this article or revise to suit Project.

        - Steel Plates, Shapes, and Bars: ASTM A36/A36M.

        - Steel Sheet: Uncoated or electrolytic zinc coated, ASTM A879/A879M, with cold-rolled steel sheet substrate complying with ASTM A1008/A1008M, Commercial Steel (CS), exposed.

        - Metallic-Coated Steel Sheet: ASTM A653/A653M, Commercial Steel (CS), Type B; with minimum G60 (Z180) or A60 (ZF180) metallic coating.

Retain the more expensive "Type 316" option in "Stainless Steel Plate, Sheet, and Strip" or "Stainless Steel Flat Bars" Paragraph below for more corrosion resistance; verify availability with manufacturers.

        - Stainless Steel Plate, Sheet, and Strip: ASTM A240/A240M or ASTM A666, [Type 304] [Type 316]. Remove tool and die marks and stretch lines, or blend into finish.

        - Stainless Steel Flat Bars: ASTM A666, [Type 304] [Type 316]. Remove tool and die marks and stretch lines, or blend into finish.

        - Aluminum Extrusions: ASTM B221 (ASTM B221M), Alloy 6063.

        - Aluminum Sheet: ASTM B209 (ASTM B209M), alloy and temper recommended by aluminum producer and finisher for type of use and finish indicated.

        - Frame Anchors: Same material as door face.

        - Inserts, Bolts, and Anchor Fasteners: Hot-dip galvanized steel in accordance with ASTM A153/A153M or ASTM F2329.

      - FABRICATION

        - General: Provide access door and frame assemblies manufactured as integral units ready for installation.

        - Metal Surfaces: For metal surfaces exposed to view in the completed Work, provide materials with smooth, flat surfaces without blemishes. Do not use materials with exposed pitting, seam marks, roller marks, rolled trade names, or roughness.

        - Doors and Frames: Grind exposed welds smooth and flush with adjacent surfaces. Furnish mounting holes, attachment devices and fasteners of type required to secure access doors to types of supports indicated.

Retain or revise two subparagraphs below to suit Project.

          - For concealed flanges with drywall bead, provide edge trim for gypsum panels securely attached to perimeter of frames.

          - For concealed flanges with plaster bead for full-bed plaster applications, provide zinc-coated expanded-metal lath and exposed casing bead welded to perimeter of frames.

        - Recessed Access Doors: Form face of panel to provide recess for application of applied finish. Reinforce panel as required to prevent buckling. Provide access sleeves for each latch operator and install in holes cut through finish.

Retain subparagraph below for recessed access doors with plaster infill.

          - For recessed doors with plaster infill, provide self-furring expanded-metal lath attached to door panel.

        - Latch and Lock Hardware:

          - Quantity: Furnish number of latches and locks required to hold doors tightly closed.

          - Keys: Furnish two keys per lock and key all locks alike.

Retain "Mortise Cylinder Preparation" Subparagraph below if lock is not provided by access door and frame manufacturer.

          - Mortise Cylinder Preparation: Where indicated, prepare door panel to accept cylinder specified in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification)."]

Retain "Aluminum" Paragraph below for aluminum access doors.

        - Aluminum: After fabrication, apply manufacturer's standard protective coating on aluminum that will come in contact with concrete.

      - FINISHES

        - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

        - Protect mechanical finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

        - Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

        - Painted Finishes: Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

          - Factory Primed: Apply manufacturer's standard, lead- and chromate-free, universal primer immediately after surface preparation and pretreatment.

          - Factory Finished: Apply manufacturer's standard baked-enamel or powder-coat finish immediately after cleaning and pretreating, with minimum dry-film thickness of 1 mil (0.025 mm) for topcoat.

Retain first option in "Aluminum Finish Color" Subparagraph below for JL Industries standard powder-coat finish color; or select from others for manufacturers optional colors.

            - Aluminum Finish Color: [White (W)] [AMS Beige (AB)] [Black (BK)] [Bronze (B)] [Flat Beige (SB)] [Flat Black (FB)] [Gray (G)] [Red (R)] [Sand (S)] [Silver (SI)]

Retain first option in "Galvanized Steel Finish Color" Subparagraph below for JL Industries standard powder-coat finish color; or select from others for manufacturers optional colors.

            - Galvanized Steel Finish Color: [White (W)] [AMS Beige (AB)] [Black (BK)] [Bronze (B)] [Flat Beige (SB)] [Flat Black (FB)] [Gray (G)] [Red (R)] [Sand (S)] [Silver (SI)].

Retain "Galvannealed Finish Color" Subparagraph below with JL Industries galvannealed steel electrolytic powder-coat finished access doors.

            - Galvannealed Steel Finish Color: [Black (BK)] [Flat Black (FB)] [AMS Beige (AB)] [Brass (BA)] [Bronze (B)] [Bronze Textured (BT)] [Sand (S)] [SC Beige (SB)] [Gray (G)] [Gray Hammertone (GH)] [Gray Textured (GT)] [Orange (O)] [Red (R)] [Red Hammertone (RH)] [Red Textured (RT)] [Silver (SI)] [White Hammertone (WH)] [White (W)] [Yellow (Y)].

        - Stainless Steel Finishes:

          - Surface Preparation: Remove tool and die marks and stretch lines, or blend into finish.

ASTM A480/A480M No. 4 finish is standard for stainless steel flush access doors; confirm availability of other finishes with manufacturers.

          - Polished Finish: ASTM A480/A480M No. 4 finish. Grind and polish surfaces to produce uniform finish, free of cross scratches.

            - Run grain of directional finishes with long dimension of each piece.

            - When polishing is completed, passivate and rinse surfaces. Remove embedded foreign matter and leave surfaces chemically clean.

Retain "Bright, Cold-Rolled, Unpolished Finish" Subparagraph below for nondirectional finish. Below is available on exterior access doors and some other products; confirm with manufacturers.

          - Bright, Cold-Rolled, Unpolished Finish: ASTM A480/A480M No. 2B.

- EXECUTION

      - EXAMINATION

        - Examine substrates for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Comply with manufacturer's written instructions for installing access doors and frames.

      - FIELD QUALITY CONTROL

Retaining second option in "Inspection Agency" Paragraph below is typical. If retaining second option in "Inspection Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals."

        - Inspection Agency: [Owner will engage] [Engage] a qualified inspector to perform inspections and to furnish reports to Architect.

        - Inspections:

          - Fire-Rated Door Inspections: Inspect each fire-rated access door in accordance with NFPA 80, Section 5.2.

        - Repair or remove and replace installations where inspections indicate that they do not comply with specified requirements.

        - Reinspect repaired or replaced installations to determine if replaced or repaired door assembly installations comply with specified requirements.

        - Prepare and submit separate inspection report for each fire-rated access door indicating compliance with each item listed in [NFPA 80] [and] [NFPA 101].

      - ADJUSTING

        - Adjust doors and hardware, after installation, for proper operation.

Insert Access Door and Frame Schedule here if required.

END OF SECTION 083113