# Fire Vents - Guide Specifications

# SECTION 07 72 36            (1995 - 07725)

# PART 1: GENERAL

1.01    RELATED DOCUMENTS

A.     Conditions of the Contract and portions of Division One of this Project Manual apply to this Section as though repeated herein.

# 1.02    SUMMARY

Select one or more of the following subparagraphs as required by the Project.

A.     Section Includes:

1.      UL Approved/UL Listed Double Leaf Fire Vent.

2.      UL Approved Double Leaf Domed Fire Vent.

3.      Gravity Ventilator Curb Mounted Fire Vent.

4.      Domed Fire Vent.

# 1.03    SUBMITTALS

A.  Product Data: For each type of fire vent indicated.  Include manufacturer's model number and accessories and requirements for roughing-in dimensions.

# 1.04    DELIVERY, STORAGE AND HANDLING

A.    Packing, Shipping, Handling and Unloading: Deliver fire vent as a factory assembled unit in manufacturer’s original packaging.

B.   Store materials in a dry, protected, well-vented area.  The contractor shall thoroughly inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

# PART 2: PRODUCTS

2.01    MANUFACTURER

A.   J L Industries, Incorporated

4450 West 78th Street Circle

### Bloomington, MN 55435

Telephone: (952) 835-6850/(800) 554-6077

FAX: (952) 835-2218

WEB: WWW.JLINDUSTRIES.COM

2.02    MANUFACTURED UNITS

A.  UL Listed Double Leaf Fire Vent.

Select one or more of the following for each UL listed double leaf fire vent size. If more than one size is required for the project, identify each type on a schedule located on the drawings and identify each type in the specification section. Custom sizes are available.

1.   Model: UFV-1; 48 inches by 48 inches clear opening.

2.   Model: UFV-2; 48 inches by 72 inches clear opening.

3.   Model: UFV-3; 48 inches by 90 inches clear opening.

4.   Model: UFV-4; 48 inches by 96 inches clear opening.

5.   Model: UFV-5; 60 inches by 60 inches clear opening.

6.  Model: UFV-6; 60 inches by 96 inches clear opening.

.

15. Characteristics:

a.   Curbs and Curb Frame: 14 gauge galvanized steel; fully welded; gasketed; insulated.

b.   Covers: 11 gauge aluminum with heavy gauge 3/16 inch aluminum pivot hinges; insulated.

c.   Finish: Factory primed.

Higher temperature fusible links are available upon request.

d.   Fusible Link: 165° F; UL listed.

e.   Drives: Torsion springs.

f.    Speed Control: Shock absorbers.

g.   Manual Operation: Interior and exterior pull handles.

B.  UL Listed Double Leaf Domed Fire Vent.

Select one or more of the following for each UL listed double leaf domed fire vent size. If more than one size is required for the project, identify each type on a schedule located on the drawings and identify each type in the specification section. Custom sizes are available.

1.   Model: UDFV-1; 48 inches by 48 inches clear opening.

2.   Model: UDFV-2; 48 inches by 72 inches clear opening.

3.   Model: UDFV-3; 48 inches by 90 inches clear opening.

4.   Model: UDFV-4; 48 inches by 96 inches clear opening.

5.   Model: UDFV-5; 60 inches by 60 inches clear opening.

6.   Model: UDFV-6; 60 inches by 96 inches clear opening.

8.   Characteristics:

a.   Curbs and Curb Frame: 14 gauge galvanized steel; fully welded; gasketed; insulated.

b.   Covers: 11 gauge aluminum with heavy gauge 3/16 inch aluminum pivot hinges; insulated.

c.   Dome Frame: 0.072 inch aluminum with self-contained sloping condensation and weepage gutter.

d.   Dome: One piece [clear] [translucent] acrylic dome.

e.   Finish: Factory primed.

Higher temperature fusible links are available upon request.

f.    Fusible Link: 165° F; UL listed.

g.   Drives: Torsion springs.

h.   Speed Control: Shock absorbers.

i.    Manual Operation: Interior and exterior pull handles.

# PART 3: EXECUTION

3.01    EXAMINATION

A.  Examine areas and conditions affecting installation.  Do not proceed with installation until unsatisfactory conditions have been corrected.

3.02    INSTALLATION

A.  Install system level and plumb, and in accord with manufacturer’s written instructions, original design and referenced standards.

# 3.03    ADJUSTING

A.  Adjust for proper operation. Replace any parts that prevent the fire vent from operating properly.

3.04    CLEANING & MAINTENANCE

A.  	Remove all debris caused by installation of the fire vent. Clean all exposed surfaces to as fabricated condition and appearance.

B. 	MAINTENANCE: Test outside and inside manual operation of latches.  Pull handles with quick jerking motion to release.  Adjust (if required) latch keepers to insure full secure latching in closed operation and simultaneous release of latches for both outside and inside operation.Periodically clean latches and strikes of old grease and dirt and reapply new grease as needed. Clean acrylic domes with a mild soap and water solution - do not use abrasive cleaners or cleaning cloths. Replace fusible links when needed by compressing release device.  Install new fusible link and close doors.

3.05    PROTECTION

A.  Provide protection of the completed installation until completion of the project. Repair any damage at no additional cost.