This guide specification was prepared utilizing 3-part format recommended by the Construction Specifications Institute (CSI), and generally incorporates recommendations from their SectionFormat™/Page Format™, and MasterFormat™, latest Editions, insofar as practicable. Carefully review and edit the text to meet the Project requirements and coordinate this Section with the remainder of the Specifications and the Drawings. Where bracketed text is indicated, e.g. [text], make appropriate selection and delete the remainder of text within additional brackets, highlighting, and bold face type, if any. Consult the manufacturer for assistance in editing this guide specification for specific Project applications where necessary. This Specification was current at the time of publication but is subject to change. Please confirm the accuracy of these specifications with the manufacturer prior to use.

SECTION 07 72 33

ROOF ACCESSORIES

PART 1 - GENERAL

  - SUMMARY

- Section Includes:

## RHD DIAMOND HATCH SERIES – ROOF HATCH

## RHDG-STH SERIES – RHDG ROOF HATCH WITH SAFETY RAILING

### ACCESSORIES:

### RSHWB AND RHSWC

### SAFETY RAILINGS

- SAFETY POSTS

- Related Sections

- Section Includes: Furnish and install factory fabricated roof hatches.

- Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SPECIFIER: Revise section numbers and titles in subparagraphs below per CSI MasterFormat™ and Project requirements.

## Related Sections: Other specification sections which directly relate to the work of this section include, but are not limited to, the following:

1. 	Section 05 50 00 - Metal fabrications for metal vertical ladders, ships’ ladders and stairs for access to roof hatches

2. 	Section 07 01 40 – Maintenance Roofing

3.	Section 07 01 70 – Operation and Maintenance of Roofing Specialties and 				Accessories

4.	Section 07 06 70 – Schedules for Roof Specialties and Accessories

5.	Section 07 22 00 – Roof and Deck Installation

6.	Section 07 26 00 – Vapor Retarders

7.	Section 07 27 00 – Air Barriers

8.	Section 07 50 00 – Membrane Roofing

9.	Section 07 81 00 – Roofing Specialties

10.	Section 07 72 00 – Roofing Accessories

11.	Section 07 72 43 – Roofing Walkboards

12.	Section 07 72 46 – Roofing Walkways

13.	Section 08 71 00 – Hardware: For Lock Type Furnished by Others

14.	Section 09 91 00 – Painting: For Field Painting of Roof Hatches

1.02	Allowances

SPECIFIER: Retain products and work included in this Section that are covered by cash or quantity allowance.  Do not include amounts.  Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the allowance.

A.	Roof hatches are part of a roof access and equipment hatch allowance.

1.03	Reference Standards

1.	The following standards and publications are applicable to the extent referenced in the 			text.

2.	American Society of Testing and Materials (ASTM) and Others:

a.	ASTM A36/A36M-12, Standard Specification for Carbon Structural Steel

b.	ASTM A153/A153M-09, Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware

c.	ASTM A653/A653M-11, Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy Coated (Galvannealed) by the Hot-Dip Process

d.	ASTM A879/A879M-12, Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Applications Requiring Designation of the Coating Mass on Each Surface

e.	ASTM A1008/A1008M-12a, Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable

f.	ASTM B209-10, Standard Specification for Aluminum and Aluminum-Alloy Sheet

and Plate

g.	ASTM B221-12a, Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes

h.	ASTM F2329-11, Standard Specification for Zinc Coating, Hot-Dip, Requirements for Application to Carbon and Alloy Steel Bolts, Screws, Washers, Nuts, and Special Threaded Fasteners

i.	ASTM C1289-17, Standard Specification for Faced Rigid Cellular Polyisocyanurate Thermal Insulation

3.	International Code Council (ICC)

a.	International Building Code (IBC)

1.04	ACTION SUBMITTALS

SPECIFIER:  Revise Section number in the paragraph below to match that used in the Project Manual.

A.	Submit in accordance with Section [01 33 00] [other]:

1.	Product Data:

a.	Materials description for roof hatches including details showing mounting type, relationships to surrounding construction, hatch type, materials, and construction, and locking features.

b.	Installation instructions for each product specified.

2.	Shop Drawings:

a.	Include details of each hatch type, size and description of components, materials, attachment devices, description of frame and finish and construction details.

b.	Schedule showing each type of hatch, locations, sizes, latching or locking provisions, and other data pertinent to installation

c.	Indicate installation procedures and accessories required for a complete installation.

SPECIFIER:  Delete subparagraph below for standard steel or galvanized steel hatches; retain for aluminum or other factory-finished products.

3.	Samples:  For each roof hatch curb section, 12 inches high by 4 inches wide in size, and in specified finish.

1.05	QUALITY ASSURANCE

A.	Regulatory Requirements:

1.	OSHA 29 CFR 1910.23 Walking-Working Surfaces, Ladders

3. 	OSHA 29 CFR 1910.25 Walking-Working Surfaces, Stairways

4.	OSHA 29 CFR 1910.28 Walking-Working Surfaces – Duty to have Fall Protection

5. 	OSHA 29 CFR 1910.29 Walking-Working Surfaces – Fall Protection Systems

6.	International Building Code (IBC) Section 1015.7 Roof Access

7.	International Building Code (IBC) Section 1011.12 Means of Egress, Stairway to Roof

8.	International Building Code (IBC) Section 1011.13 Means of Egress, Guards

B.	Comply with standards referenced in Article 1.03 REFERENCES.

C.	Provide roof hatches produced by a single manufacturer.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Deliver, store, and handle roof hatches using means and methods that will prevent damage, deterioration, or loss.

1.	Deliver units in manufacturer's original packaging, properly labeled for identification.

PART 2 - PRODUCTS

2.01	ROOF HATCH MANUFACTURERS

A.	Acceptable Manufacturers:

JL Industries – Part of Activar Construction Products Group, Inc.

9702 Newton Av South

Bloomington, MN  55431

(800) 554-6077

www.activarcpg.com

sales@activarcpg.com

B.	Substitutions:  Manufacturers seeking approval of their products are required to comply with the Owner's Instructions to Bidders, generally contained in the Project Manual.

2.02		RHDG Diamond Series – Galvanneal Steel Roof Hatch

- Style RHDG: Galvanneal steel, insulated roof hatch cover and roof curb.

  - Model No. RHDG [insert remainder of model number from subparagraph 4 below].

  - Performance Criteria: Tested and approved to support a minimum live load of 40 pounds per square foot (195 kilograms per square meter).

  - Cover: Insulated, 14-gauge (1.99 mm) galvanneal steel exterior, welded cover with 22-gauge liner. Door opens 75 degrees.

    - Continuous weatherproof EPDM sponge rubber adhesive-backed gasket.

    - Insulation: 1-inch polyisocyanurate with thermal resistance R-6.

- Curb: Insulated, 14-gauge (1.99 mm) galvanneal steel single wall curb and counterflashing with Diamond Grip™ feature to secure roof membrane. 12 inches (305 mm) high, 3-1/2 inches (88.9 mm) wide flange for securing to roof. Insulation: 1-inch polyisocyanurate with thermal resistance R-6.

  - Hold-open arm: Clear zinc-plated steel hold-open arm.

  - Latch: Clear zinc-plated steel slam latch with inside and outside handles and padlock hasps. Tested to 50 pounds per square foot (244 kg per square meter) wind uplift.

  - Finish: White textured powder coat.

  - Hatch Opening Size (width x height) and Weight:

- RHDG-1WT: 36 inches X 30 inches (914 mm x 762 mm); (138 lbs.)

- RHDG-2WT: 30 inches x 54 inches (762 mm x 1372 mm); (187 lbs.)

- RHDG-3WT: 30 inches x 96 inches (762 mm x 2438 mm); (289 lbs.)

- RHDG-4WT: 36 inches x 36 inches (914 mm x 914 mm); (162 lbs.)

- RHDG-5WT: 48 inches x 48 inches (1219 mm x 1219 mm); (232 lbs.)

- RHDG-6WT: 32 inches x 72 inches (813 mm x 1829 mm); (235 lbs.)

- RHDG-7WT: 37 inches x 30 inches (940 mm x 762 mm); (140 lbs.)

- <Insert dimensions>

  - Model RHDG Options:

SPECIFIER:  Select specific options listed below, if desired.

- Energy-efficient polyisocyanurate insulation 1-1/2 inches on curb walls (R-9).

- 3/4-inch wood pine nailer on curb walls

- 1-inch fiberboard insulation on curb walls

- Curb double wall

- Curb heights, choose from 13 inches up to 22 inches in height; [____ inches]

- Galvanneal steel curbs with aluminum covers

- Stainless steel type 316 hinge pins

- Stainless steel type 316 hardware

- Finish color options: [Gray Textured], [Red Textured], [Bronze Textured]

2.03	RHDA Diamond Series – Aluminum Roof Hatch

A.		Style RHDA: Aluminum, insulated roof hatch cover and roof curb.

- Model No. RHDA [insert remainder of model number from subparagraph 9 below].

- Performance Criteria: Tested and approved to support a minimum live load of 40 pounds per square foot (195 kilograms per square meter).

- Cover: Insulated, 11-gauge aluminum exterior, welded cover with 18-gauge liner. Door opens 75 degrees.

  - Continuous weatherproof EPDM sponge rubber adhesive-backed gasket.

  - Insulation: 1 inch polyisocyanurate with thermal resistance R-6.

- Curb: Insulated, 11-gauge aluminum single wall curb and counterflashing with DiamondGrip™ feature to secure roof membrane. 12 inches (305 mm) high, 3-1/2 inches (88.9 mm) wide flange for securing to roof. to secure roof membrane

- Hold Open Arm: Clear zinc-plated steel hold-open arm.

- Latch: Clear zinc-plated steel slam latch with inside and outside handles and padlock hasps. Tested to 50 pounds per square foot (244 kg per square meter) wind uplift.

- Finish: Mill finish.

- Hatch Opening Size (width x height) and Weight:

- RHDA-1:	36 inches X 30 inches ( 914 mm x 762 mm); (68 lbs.)

- RHDA-2:	30 inches x 54 inches (762 mm x 1372 mm); (88 lbs.)

- RHDA-3:	30 inches x 96 inches (762 mm x 2438 mm); (133 lbs.)

- RHDA-4: 	36 inches x 36 inches (914 mm x 914 mm); (76 lbs.)

- RHDA-5: 	48 inches x 48 inches (1219 mm x 1219 mm); (111 lbs.)

- RHDA-6: 	32 inches x 72 inches (813 mm x 1829 mm); (110 lbs.)

- RHDA-7: 	37 inches x 30 inches (940 mm x 762 mm); (69 lbs.)

- <Insert dimensions>

- Model RHDA Options:

SPECIFIER:  Select specific options listed below, if desired.

- Energy-efficient polyisocyanurate insulation 1-1/2 inches on curb walls (R-9).

- 3/4-inch wood pine nailer on curb walls

- 1-inch fiberboard insulation on curb walls

- Curb double wall

- Curb heights, choose from 13 inches up to 22 inches in height; [___ inches]

- Galvanneal steel curbs with aluminum covers

- Stainless steel type 316 hinge pins

- Stainless steel type 316 hardware

- Finish color options: [Gray Textured], [Red Textured], [Bronze Textured]

- Polyvinylidene Fluoride PVDF, 70% Fluoropolymer [10 year],[20 year] select from color chart

2.04	RHTB ThermalBlock Series – Thermally Broken Roof Hatch

A.		Style RHTB: Thermally broken aluminum roof hatch cover and roof curb.

- Model No. RHTBA [insert remainder of model number from subparagraph 7 below].

- Performance Criteria: Tested and approved to support a minimum live load of (195 kilogram per square meter)

- Cover: Aluminum cover (0.09 inch/2.3mm). Both interior and exterior surface is thermally broken. Cover has continuous extruded EPDM acoustical rated gasketing.

  - Cover Insulation: 3 inches of foil-faced rigid polyisocyanurate insulation with R-value 20.

  - Liner: Aluminum liner cover (0.0907 inch /2.3mm).

- Curb: Aluminum (0.0907 inch (2.3mm) with single wall curb, integral metal flashing, same gauge, fully welded corners, counter flash 9 inches on center (228 mm), to be bent inward to hold single ply roofing membrane.

  - Curb fabricated a minimum height of 12 inches (305 mm) above roof surface.

  - Sloping Roofs: Where slope of roof deck exceeds 7:12, fabricate curb with perimeter curb height that is tapered to accommodate roof slope so that top surfaces of perimeter curb are level.

  - Curb Insulation: 3 inches (76 mm) of single layer rigid polyisocyanurate insulation R-value = 20.

- Hardware:

  - Hinge: Pintle hinge with stainless steel hinge pin.

  - Spring: Gas spring with integrated damper.

  - Hold-Open Arm: Automatic hold open arm, zinc plated steel with red vinyl grip handle cover.

  - Latch: Zinc plated steel spring type slam latch with inside and outside operating turn handles and padlock hasp.

- Finish: Mill finish.

- Hatch Opening Size (width x height) and Weight:

- RHTBA-1: 36 inches x 30 inches (900 mm x 750 mm); (107 lbs.)

- RHTBA-2: 30 inches x 54 inches (750 mm x 1370 mm); (128 lbs.)

- RHTBA-3: 30 inches x 96 inches (2438 mm x 762 mm); (172 lbs.)

- RHTBA-4: 36 inches x 36 inches (900 mm x 900 mm); (145 lbs.)

- RHTBA-5: 48 inches x 48 inches (1220 mm x 1220 mm); (235 lbs.)

- Model RHTBA Options:

SPECIFIER:  Select specific options listed below, if desired.

- Curb Double Wall

  - RHDG-STH SERIES - COMBINATION ROOF HATCH AND SAFETY RAIL SYSTEM

- Style RHDG-STH:  Self-attaching galvanneal steel roof hatch with bolt-on safety rail system.

- RHDG-[X]-STH:  insert remainder of model number from subparagraph 4 below].

- Roof Hatch:

  - Performance Criteria: Tested and approved to support a minimum live load of 40 pounds per square foot (195 kilogram per square meter).

  - Cover: Insulated, 14-gauge (1.99 mm) galvanneal steel exterior, welded cover with 22-gauge liner. Door opens 75 degrees.

    - Continuous weatherproof EPDM sponge rubber adhesive backed gasket.

    - Insulation: 1 inches polyisocyanurate with thermal resistance R-6.

  - Curb: Insulated, 14-gauge (1.99 mm) galvanneal steel single wall curb and counterflashing with DiamondGrip feature. 12 inches (305 mm) high, 3-1/2 inches (88.9 mm) wide flange for securing to roof. to secure roof membrane

  - Hold-open arm: Clear zinc-plated steel hold-open arm.

  - Latch: Clear zinc-plated steel slam latch with inside and outside handles and padlock hasps. Tested to 50 pounds per square foot (244 kg per square meter) wind uplift.

  - Finish: White textured powder coat.

- Bolt-On Safety Railing: Designed to bolt on the curb counterflashing and does not penetrate the curb protecting the integrity of the roof membrane.

  - Certification: Meets OSHA required compliance for safe egress and ingress through rooftop hatch openings while hatch is in use; complies with OSHA CFR 29-1910.28 and CFR 29-1910.29.

  - Rail: Material: 1-⅝" x .065" (16 gauge) galvanized steel tubing

  - Bracket Material: 2" x 2" square galvanized steel tubing 1/4" and 1/2" plate CRS

  - Finish: Yellow powder coat

  - Hinges: Steel, adjustable spring hinges

  - Gate: Self-closing, self-latching with telescoping size adjustment

  - Latch: Steel, black powder coat pin hooks around gravity latch catch

  - Hardware: Black plastic tubing caps and zinc plated steel hardware.

- Hatch Opening Size and Total Weight with Rail:

  - RHDG-1WT-STH:  36 inches by 30 inches (914 mm by 762 mm); 183 lbs.(84 kg).

  - RHDG-2WT-STH:  30 inches by 54 inches (762 mm by 1372 mm); 245 lbs. (112 kg).

  - RHDG-3WT-STH:  30 inches by 96 inches (762 mm by 2438 mm); 315 lbs. (143 kg).

  - RHDG-4WT-STH:  36 inches by 36 inches (914 mm by 914 mm); 219 lbs. (100 kg).

  - RHDG-5WT-STH:  48 inches by 48 inches (1219 mm by 1219 mm); 298 lbs. (136 kg).

  - ACCESSORIES

- RSHWB SERIES – SAFETY RAILING FOR NEW HATCHES

  - Style RSHWB:  A bolt-on safety railing designed to bolt on the curb counterflashing and does not penetrate the curb protecting the integrity of the roof membrane.

- Model No. RSHWB [insert remainder of model number from subparagraph j below]

- Certification:  Meets OSHA required compliance for safe egress and ingress through rooftop hatch openings while hatch is in use; complies with OSHA CFR 29-1910.28 and CFR 29-1910.29.

- Material: 1-⅝" x .065" (16 gauge) galvanized steel tubing

- Bracket Material: 2" x 2" x.048" (18 gauge) square galvanized steel tubing

- Finish: Yellow powder coat

- Hinges: Steel, adjustable spring hinges

- Gate: Self-closing, self-latching with telescoping size adjustment

- Latch: Steel, black powder coat pin hooks around gravity latch catch

- Hardware: Black plastic tubing caps and zinc-plated steel hardware

- Hatch Opening Size, Railing Weight, and Installs to Hatch Model Noted:

- RSHWB-1LY: 36 inches by 30 inches (914 mm by 762 mm); 74 lbs. (33.5 kg); Designed to fit Models RHDG/RHDA-1.

- RSHWB-2WY: 30 inches by 54 inches (762 mm by 1372 mm); 81 lbs. (36.7 kg); Designed to fit Models RHDG/RHDA-2.

- RSHWB-3WY: 30 inches by 96 inches (762 mm by 2438 mm); 107 lbs. (37 kg); Designed to fit Models RHDG/RHDA-3.

- RSHWB-4LY: 36 inches by 36 inches (914 mm by 914 mm); 77 lbs. (48.5 kg); Designed to fit Models RHDG/RHDA-4.

- RSHWB-5LY: 48 inches by 48 inches (1219 mm by 1219 mm); 84 lbs. (38.1 kg); Designed to fit Models RHDG/RHDA-5.

- <Insert dimensions>

B.	RSHWC SERIES - SAFETY RAILING FOR ROOF HATCHES

  - Style RSHWC: A compression-style safety railing designed to mount onto the curb counterflashing with adjustable width and length to accommodate other manufacturer's designs

    - Model No.  SHWC- [insert remainder of model number from subparagraph j. below].

    - Certification:  Meets OSHA required compliance for safe egress and ingress through rooftop hatch openings while hatch is in use; complies with OSHA CFR 29-1910.28 and CFR 29-1910.29.

    - Material: 1-⅝" x .065" (16 gauge) galvanized steel tubing

    - Bracket Material: 2" x 2" x.048" (18 gauge) square galvanized steel tubing

    - Finish: Yellow powder coat

    - Hinges: Steel, adjustable spring hinges

    - Gate: Self-closing, self-latching with telescoping size adjustment

    - Latch: Steel, black powder coat pin hooks around gravity latch catch

    - Hardware: Black plastic tubing caps and zinc-plated steel hardware

    - Hatch Opening Size, Railing Weight, and Installs to Hatch Model Noted:

i.	RSHWC-1LY: 36 inches by 30 inches (914 mm by 762 mm); 74 lbs. (30 kg); Designed to fit Models RHDG/RHDA-1.

ii.	RSHWC-2WY: 30 inches by 54 inches (762 mm by 1372 mm); 81 lbs. (32 kg); Designed to fit Models RHDG/RHDA-2.

iii.	RSHWC-3WY: 30 inches by 96 inches (762 mm by 2438 mm); 107 lbs. (37 kg); Designed to fit Models RHDG/RHDA-3.

iv.	RSHWC-4LY: 36 inches by 36 inches (914 mm by 914 mm); 77 lbs. (31 kg); Designed to fit Models RHDG/RHDA-4.

v.	RSHWC-5LY: 48 inches by 48 inches (1219 mm by 1219 mm); 84 lbs. (35 kg); Designed to fit Models RHDG/RHDA-5.

vi.	<Insert dimensions>

C.	Ladder-Assist Safety Post (Extendable):  Preassembled steel safety post which attaches directly to the top two rungs (either square or round) of the vertical access ladder with two U-shaped bolts.

- Model LP- 4

- Post Assembly:  Square post with latch which maintains the post at variable heights, and spring coil at base to allow user to lift (extend) post with one hand.

- Post Finish: Safety yellow powder coat.

- Weight:  25 lbs.  (12 kg).

D.	Ladder-Assist Safety Post – Extension-Up Series: Preassembled steel safety post which attaches directly to the top 2 rungs (either square or round) of the vertical access ladder with 2 bolts and mounting bracket.

- Model RSLP

a. 	Post Assembly:  Square post with release latch which maintains the post securely locked into the upright position, and spring coil at base to allow user to lift (extend) post with one hand.

- Post Finish RSLP-G: Hot-dipped galvanized.

- Post Finish RSLP-Y: Powder coat painted safety yellow

- Weight 23 lbs (10.4 kg).

E. 	Ladder-Assist Safety Post – Foldable Series:  Preassembled steel safety post which attaches directly to and stows inside the roof hatch curb. Allows user to lift post and automatically lock into upright position with one hand.

- Model LP-6.

- Post Assembly:  1 ½ inches x 1 ½ inches 12 gauge steel square post attached by swivel bolt to welded 10-gauge steel mounting plate.

- Post Finish:  Safety yellow powder coat.

- Weight:  8 lbs.  (4 kg).

- Testing:  200-pound design load rating.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Examine substrates for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

1.	Notify the Contractor in writing of conditions detrimental to proper and timely completion of the installation.

2.	Verify dimensions of roof openings for roof accessories.

3.	Proceed with installation only after unsatisfactory conditions have been corrected.

3.02	INSTALLATION

A.	General:  Comply with manufacturer's written instructions for installing roof hatches and accessories, if any.

1.	Install roof hatches level, plumb, true to line and elevation, and without warping, jogs in alignment, buckling, or tool marks.

2.	Anchor roof hatches securely in place so they are capable of resisting indicated loads.

3.	Use fasteners, separators, sealants, and other miscellaneous items as required to complete installation of roof hatches and fit them to substrates.

4.	Install roof hatches to resist exposure to weather without failing, rattling, leaking, or loosening of fasteners and seals.

B.	Metal Protection:  Protect metals against galvanic action by separating dissimilar metals from contact with each other.

1.	Coat concealed side of uncoated aluminum components with bituminous coating where in contact with wood, ferrous metal, or cementitious construction.

2.	Underlayment:  Where installing roof hatches directly on cementitious or wood substrates, install a course of felt underlayment and cover with a slip sheet, or install a course of polyethylene sheet.

C.	Installation:  Install roof hatch so top surface of hatch curb is level.

SPECIFIER:  Retain subparagraphs below if roof hatches are so equipped.

1.	Attach safety railing system to roof hatch curb.

2.	Attach ladder-assist post according to manufacturer's written instructions.

D.	Surface Repairs:

SPECIFIER:  Select galvanneal surfaces or factory-painted surfaces  in subparagraphs below.

1.	Galvanized Surfaces:  Clean field welds, bolted connections, and abraded areas and repair galvanizing according to ASTM A 780.

2.	Powder Coat Painted Surfaces:  Touch up factory-painted surfaces with compatible paint.

3.03	ADJUSTING AND CLEANING

A.	Verify that roof hatches operate properly.

B.	Clean, lubricate, and adjust operating mechanism and hardware.

C.	Clean exposed surfaces according to manufacturer's written instructions.

D.	Replace roof hatches that have been damaged or that cannot be successfully repaired by finish touchup or similar minor repair procedures.

END OF SECTION