MECHANICAL INSULATION—MasterFormat 95

This section includes thermal & acoustic insulation for piping and equipment, and thermal & acoustic insulation applied to ductwork.

# This section is based on CSI MASTER FORMAT Section 15080, Mechanical Insulation, and has been revised to include Knauf Insulation products and installation recommendations.  When a project requires more detailed specification statements, one should consult Section 15083-Piping Insulation, Section 15082-Equipment Insulation, or Section 15081-Ductwork Insulation.

# PART 1—GENERAL

  - SECTION INCLUDES

- Piping Insulation, jacketing and accessories.

- Equipment insulation and jacketing or coatings.

- Ductwork insulation, jacketing and lining.

  - REFERENCES

- ASTM International – formerly known as the American Society for Testing and Materials

- ASHRAE – American Society of Heating, Refrigerating, and Air Conditioning Engineers

- NAIMA – North American Insulation Manufacturers Association

- NFPA – National Fire Protection Association

- SMACNA – Sheet Metal and Air Conditioning Contractors National Association

- UL - Underwriter’s Laboratories

- UL Environment – Underwriter’s Laboratories Environment

  - Definitions

- UL GREENGUARD provides independent, third-party, Indoor Air Quality (IAQ) certification of products for emissions of respirable particles and Volatile Organic Compounds (VOCs), including formaldehyde and other specific product-related pollutants. Certification is based upon criteria used by EPA, OSHA and WHO.

- IAQ: Indoor Air Quality

- EPA: Environmental Protection Agency

- WHO: World Health Organization

- ASJ+: All Service Jacket composed of aluminum foil reinforced with glass scrim bonded to a kraft paper interleaving with an outer film layer leaving no paper exposed.

- ASJ: All Service Jacket

- SSL+: Self-sealing Advanced Closure System

- SSL: Self-Sealing Lap

- FSK: Foil Scrim Kraft; jacketing

- PSK: Poly Scrim Kraft; jacketing

- PVC: Polyvinyl Chloride

- FRP: Fiberglass Reinforced Plastic

- Glass Mineral Wool:  Interchangeable with fiber glass, but replacing the term with the intent to disassociate and differentiate Glass Mineral Wool from the potential health and safety risk of special purpose or reinforcement products that do not meet the bio soluble criteria of
insulation made from glass.

- ECOSE® Technology: a revolutionary new binder system based on rapidly renewable

bio-based materials rather than petroleum-based chemicals commonly used in other glass mineral wool insulation products. ECOSE® Technology reduces the binder embodied energy by up to 70% and does not contain phenol, formaldehyde, acrylics or artificial colors.

- UL GREENGUARD Gold Certification: (Formerly known as GREENGUARD Children & Schools Certification) offers stricter certification criteria, considers safety factors to account for sensitive individuals (such as children and the elderly) and ensures that a product is acceptable for use in environments such as schools and healthcare facilities. It is referred by both The Collaborative for High Performance Schools (CHPS) and the Leadership in Energy and Environmental Design (LEED) Building Rating Systems.

- UL Environment Formaldehyde Free Verification Requirements: for a product to be verified as formaldehyde free, product samples must have a measured emission factor of less than or equal to 5 µg/m2 h at 24 elapsed hours or 3 µg/m2 h at 336 elapsed hours. An emission factor of 5 µg/m2 h corresponds to a measured chamber concentration of 2.5 µg/m3 for a typical loading ratio of 0.5 m2/m3   This chamber concentration is comparable to, or below typical outdoor air concentrations. This demonstrates that the formaldehyde exposure from products labeled as formaldehyde free will not contribute to airborne formaldehyde concentrations at greater levels than those found in the natural outdoor environment.

Declare and The Living Building Challenge – The Living Building Challenge is a philosophy, advocacy tool and certification program that addresses development at all scales. The purpose of The Living Building Challenge is to define the most advanced measure of sustainability in the built environment today and acts to diminish the gap between current limits and ideal solutions. Declare supports The Living Building Challenge by providing a transparent materials database that project teams can select from to meet Imperative 11.

- Imperative 11, Red List – requires that manufacturers disclose the ingredients in their

products to insure that they are free of Red List chemicals and materials. The Red List represents the “worst in class” materials, chemicals and elements known to pose serious risks to human health and the greater ecosystem.

- Underwriter’s Laboratories Environment (UL Environment): offers independent green claims validation, product assessment and certification. UL GREENGUARD provides third-party credibility for sustainable products.

- UL Environment Claims Validation (ECV): service and label tests a manufacturer’s product and validates that the environmental claims they make in their marketing and packaging materials are factual. This ECV service will allow manufacturers to verify their products contain a quantifiable amount of recycled content and, as such help limit raw material extraction and reduce landfill waste. It will also enable products to qualify for LEED®

MR Credit 4 Recycled Content LEED-NC 2009 or New LEED V-4 Building product disclosure and optimization – sourcing of raw materials.

- EUCEB: Exonerated fiber from a health and safety standpoint by the European Certification Board process.

- Recycled Content – Post-Consumer: materials such as bottled glass collected at curbside or other collection sites after consumer use and used in the manufacturing process to create a new product rather than being placed in a landfill or incinerated.

- Recycled Content – Pre-Consumer (aka Post-Industrial): materials used or created from one manufacturing process which are collected as scrap and placed back into another manufacturing process rather than being placed in a landfill or incinerated.

- Polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE and Deca-BDE fire retardants: have been linked to adverse health effects after exposure in low concentrations.

- UL Classified: UL has tested and evaluated samples of the product with respect to certain properties of the product. UL classifies products to:

Applicable UL requirements

Standards for safety

Standards of other National and International organizations

Y.  EPD: Environmental Product Declaration. A third party verified document that reports 
           environmental data of products based on the Life Cycle Assessment (LCA) and other  
           relevant information, and in accordance with the International Standard ISO 14025
           (Type III Environmental Declarations)

  - SUBMITTALS FOR INFORMATION

- Product data: To include product description, manufacturer's installation instructions, types and recommended thicknesses for each application, and location of materials.

- Samples and mockups of systems shall be provided upon engineer’s request.

- EPD Submittals: As Certified by UL Environment.

- LEED Submittals:

1.	Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including   
printed statement of VOC content and chemical components.

2.	Product Data for Credit MR 5 Regional Materials: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

3.	LEED v 4, Product Data for Credit EA 2: For products and materials significant to the energy performance of a structure, provide documentation that indicates that insulation levels are significant to increasing the level of energy performance beyond the prerequisite standard.

4.	LEED v 4, Product Data for Credit MR 2: For products and materials to comply with Building Product Disclosure & Optimization, provide data/evidence that substantiates Environmental Product Declaration and Multi Attribute Optimization requirements.

5.	LEED v 4: Product Data for Credit MR 3: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

6.	LEED v 4, Product Data for Credit MR 4: For products having recycled content documentation; indicating percentages by weight of post-consumer and pre-consumer recycled content. Include statement indicating cost for each product having recycled content.

7.	LEED v 4, Product Data for Credit EQ 2:  For products and materials to comply with low emittance standards, provide documentation substantiating that insulation products comply with requisite low emittance standards.

8.	LEED v 4, Product Data for Credit EQ 5: For products and materials to meet the standard for both thermal comfort design and thermal comfort control, provide data to support that insulation products are significant to thermal comfort design and thermal comfort control.

9.	LEED v 4, Product Data for Credit EQ 9: For products and materials that contribute to the design and performance of workspaces that promote occupants well-being, productivity, and communication, provide data/documentation supporting acoustical benefits of Glass Mineral Wool insulation products.

10.	Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that product complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small Scale Environmental Chambers."

  - ENVIRONMENTAL REQUIREMENTS

- Maintain ambient conditions required by manufacturers of tapes, adhesives, mastics, cements, and insulation materials.

- Insulation and related materials shall have surface burning characteristics determined by test performed on identical products per UL 723 or ASTM E 84 mounted and installed as per        ASTM E 2231. All testing shall be performed by a testing and inspecting agency acceptable to authorities having jurisdiction. Insulation, jacket materials, adhesives, mastics, tapes and cement material containers shall be labeled with appropriate markings of applicable testing and inspecting agency.

1.   Insulation installed indoors: Flame spread index of 25 or less, and smoke developed index of 50 or less.

2.   Insulation installed outdoors: Flame spread index of 75 or less, and smoke developed index of 150 or less.

- Follow manufacturer’s recommended handling practices.

- Supply glass mineral wool products that are manufactured using a minimum of 50% “post-consumer” recycled material.

- Supply glass mineral wool products that are manufactured using a bio-based binder rather than non-renewable petroleum-based chemicals and does not contain phenol, formaldehyde, or acrylics whenever possible.

- Supply glass mineral wool products that have achieved UL GREENGUARD Gold Certification and are verified Formaldehyde Free by UL Environment; whenever possible.

- Supply glass mineral wool products that are Living Building Challenge – Declare, Red List Free; whenever possible.

- Products shall not contain polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE fire retardants; whenever available.

- WET: Contractor shall take precaution to protect insulation materials from moisture exposure or physical damage. Any glass mineral wool insulation that becomes wet or damaged shall be replaced at no additional cost.

1.   HVAC duct work insulation used in the air stream must be discarded if exposed to liquid water.

2.   Pipe Insulation with factory applied ASJ+ facing having been fully installed with all pipe insulation system joints (including fittings, flanges, valves, and other inline devices) sealed per manufacturer’s installation recommendation which may experience casual and intermittent exposure to liquid water after installation may be exempted from removal and replacement.  Contractor must be prepared to provide proof that insulation glass fiber has not been exposed to liquid water.

J.  Insulation materials for use on austenitic stainless steel shall be qualified as acceptable

according to ASTM C 795.

K. Insulation materials for use on carbon steel shall be tested per ASTM C 1617 and the Mass

Loss Corrosion Rate (MLCR), when tested with extracted solutions, shall be equal to or less than that determined when tested with 1 ppm chloride water.

# PART 2—PRODUCTS

  - PIPE INSULATION AND ACCESSORIES

- Manufacturers: Knauf Insulation, Proto Corporation, ICA Hamfab, VentureClad or pre-approved substitute.

- Glass Mineral Wool: Knauf Insulation Earthwool™ 1000º Pipe Insulation with ECOSE® Technology, UL/ULC Classified, EPD Certified by UL Environment or Knauf Insulation Earthwool™ Redi-Klad® 1000° Pipe Insulation with ECOSE® Technology, Composite FHC 25/50 per ASTM E 84, EPD Certified by UL Environment; Living Building Challenge – Declare, Red List free for unjacketed Earthwool Pipe and composite Redi-Klad® Pipe, meeting ASTM C 547 Type IV Grade A, ASTM C 585, ASTM C411 and  ASTM C 795.

- ‘K’ (‘SI’) Value: ASTM C 335, 0.23 at 75ºF (0.033 at 24ºC) mean temperature.

- Maximum Service Temperature: 1000ºF (538ºC).

- Vapor Retarder Jacket: ASJ+/SSL+ conforming to ASTM C 1136 Type I,II, III, IV, &VIII secured with self-sealing longitudinal laps and matching butt strips.

- Redi-Klad Jacket: VentureClad 5-ply weather and abuse resistant with self-sealing lap. Zero permeability per ASTM E 96-05; puncture resistance 35.4 kg (189.3 N) per     ASTM D 1000; tear strength 4.3 lb (19.4 N) per ASTM D 624; thickness 14.5 mils (0.0145”); tensile strength 68 lb/inch width [306 N (32 kg)/25 mm].

5.   Earthwool™ 1000° Pipe Insulation verified formaldehyde free by UL Environment.

C.  Glass Mineral Wool: Knauf Pipe & Tank Insulation with ECOSE® Technology, FHC 25/50 
            per ASTM E 84; semi-rigid, limited combustible meeting requirements of ASTM C 1393;       
            NRC 1.36; ASTM C 795, ASTM C 447 and MIL-I-24244 C.

- ‘K’ (‘SI’) Value: ASTM C 335, 0.25 at 75ºF (0.036 at 24ºC) mean temperature.

- Maximum Service Temperature: 850ºF (454ºC).

- Compressive Strength: not less than 120 PSF (5.75 kPa) @ 10% deformation per

ASTM C 165.

- Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type II.

D.  Glass Mineral Wool: Knauf KwikFlex™ , UL/ULC Classified; semi-rigid glass mineral wool 
            blanket in roll form meeting requirements of UL 723, ASTM C 1393, ASTM C447 and

ASTM C 356.

- ‘K’ (‘SI’) Value:  ASTM C 516, 0.24 at 75(F (0.035 at 24(C) mean temperature.

- Maximum Service Temperature: 850(F (454(C); Maximum surface temperature for faced product: 150(F (66(C); Maximum thickness @ 850(F: 4” (102 mm).

- Compressive Strength: not less than 25 PSF (1.2 kPa) @ 10% deformation per     ASTM C 165.

- Vapor Retarder Jacket:  ASJ, FSK or PSK conforming to ASTM E 96, Procedure A.

E.   Field-Applied Jackets or Fitting Covers

- PVC: Proto Corporation 25/50 or Indoor/Outdoor, UV resistant fittings, jacketing and accessories, white or colored.  Fitting cover system consists of pre-molded, high impact PVC materials with glass mineral wool inserts. Glass mineral wool insert has a thermal conductivity (‘K’) of 0.26 at 75°F. (‘SI’ - 0.037 at 24°C) mean temperature.

- Closures: stainless steel tacks, matching PVC tape, or PVC adhesive per manufacturer’s recommendations.

- Metal: Aluminum, 0.016” (0.406 mm) thick or Stainless Steel, 0.010” (0.254 mm) thick in smooth, corrugated, or embossed finish with factory-applied moisture barrier.  Overlap shall be 2” (50 mm) minimum.  Fittings shall be die-shaped with factory-applied moisture barrier.

- Laminated Self-Adhesive Water and Weather Seals: permanent acrylic self-adhesive System; weather resistant, high puncture and tear resistance; meeting or exceeding requirements of UL 723; applied in strict accordance with manufacturers’ recommendations.

- Fire Retardants: products shall not contain polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE and Deca-BDE; whenever available.

F.   Fitting Insulation

- Pre-formed, molded, formaldehyde free glass mineral wool, and minimum 50% post-consumer recycled glass, or mitered glass mineral wool pipe insulation sections in lieu of PVC systems.  These fittings shall be further protected by field-applied PVC fitting covers, metal fitting covers, or glass fabric and mastic sealed as necessary.

2.2	EQUIPMENT INSULATION – Intermediate Temperature

- Manufacturer: Knauf Insulation or pre-approved substitute.

- Rigid Glass Mineral Wool Board: Knauf Insulation Board with ECOSE® Technology, UL/ULC Classified Plain, ASJ and FSK, FHC 25/50 per ASTM E 84 PSK only; meeting ASTM C 612 Type IA and IB; rigid.

- Maximum Service Temperature: 450ºF (232ºC).

- Verified formaldehyde free by UL Environment.

- Concealed Areas

- Density: Minimum 3 PCF (48 kg/m3).

- ‘K’ (‘SI’) Value: ASTM C 177, 0.23 at 75ºF (0.033 at 24ºC) mean temperature.

c.   Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type I, or FSK or PSK

conforming to ASTM C 1136 Type II.

- Exposed Areas

- Density: Minimum 6 PCF (96 kg/m3).

- ‘K’ (‘SI’) Value: ASTM C 177, 0.22 at 75ºF (0.032 at 24ºC) mean temperature.

- Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type I, or FSK or PSK conforming to ASTM C 1136 Type II in combination with protective jacket where necessary.

- Rigid Glass Mineral Wool Board: Knauf Elevated Temperature (ET) Board with ECOSE® Technology, UL/ULC Classified, meeting ASTM C 612 Type IA, IB, and II; rigid, noncombustible and ASTM C447.

  - Maximum Service Temperature: 1000ºF (538ºC).

  - Density: 2.8 PCF (45 kg/m3).

  - ‘K’ (‘SI’) Value: ASTM C 177, 0.25 at 100ºF (0.036 at 38ºC) mean temperature.

4.   Verified formaldehyde free by UL Environment.

- Semi-Rigid Glass Mineral Wool Board: Knauf Elevated Temperature (ET) Panel with ECOSE® Technology, UL/ULC Classified, meeting ASTM C 612 Type II and III; semi-rigid, noncombustible and ASTM C447.

- Maximum Service Temperature: 1000º F (538ºC).

- Density: 2.4 PCF (38 kg/m3).

- ‘K’ (‘SI’) Value: ASTM C 177, 0.25 at 100ºF (0.036 at 38ºC) mean temperature.

- Verified formaldehyde free by UL Environment.

- Flexible Glass Mineral Wool Blanket: Knauf Elevated Temperature (ET) Blanket with ECOSE® Technology, UL/ULC Classified; flexible, noncombustible meeting ASTM C447.

- Maximum Service Temperature: 1000ºF (538ºC).

- Density: 1.1 PCF (18 kg/m3).

- ‘K’ (‘SI’) Value: ASTM C 177, 0.28 at 100ºF (0.040 at 38ºC) mean temperature.

- Verified formaldehyde free by UL Environment.

  - DUCTWORK INSULATION

- Manufacturer: Knauf Insulation or pre-approved substitute.

- Flexible Glass Mineral Wool Blanket: Knauf Friendly Feel® Duct Wrap with ECOSE® Technology, UL/ULC Classified for FSK; FHC 25/50 per ASTM E 84 for PSK; meeting ASTM C 553 Types I, II and III, and ASTM C 1290; UL GREENGUARD Certified; flexible, limited combustible.

- ‘K’ (‘SI’) Value: ASTM C 177, 0.29 at 75ºF (0.042 at 24ºC) mean temperature.

- Verified formaldehyde free by UL Environment.

- Maximum Service Temperature

  - Faced: 250ºF (121ºC).

  - Unfaced: 350°F (177°C).

- Vapor Retarder Jacket: FSK or PSK conforming to ASTM C 1136 Type II.

- Installation: Maximum allowable compression is 25%.

- Securement: Secured in place using outward cinching staples in combination with appropriate pressure-sensitive aluminum foil or PSK tape, or in combination with glass fabric and vapor retarder mastic.

- Density:

- Concealed areas: Minimum 0.75 PCF (12 kg/m3).

b.  Exposed areas: Minimum 1.0 PCF (16 kg/m3).

- Glass Mineral Wool: Knauf KwikFlex , UL/ULC Classified for ASJ and FSK; FHC 25/50 per ASTM E 84 for PSK; semi-rigid glass mineral wool blanket in roll form meeting requirements of ASTM E 84; ASTM C 1393, ASTM C447 and ASTM C 356.

1.	‘K’ (‘SI’) Value: ASTM C 516, 0.24 at 75(F (0.035 at 24(C) mean temperature.

- Maximum Service Temperature: 850(F (454(C); Maximum surface temperature for faced product: 150(F (66(C); Maximum thickness @ 850(F: 4“ (102 mm).

- Compressive Strength: not less than 25 PSF (1.2 kPa) @ 10% deformation per      ASTM C 165.

- Vapor Retarder Jacket:  ASJ, FSK or PSK.

- Rigid Glass Mineral Wool Board: Knauf Insulation Board with ECOSE® Technology, UL/ULC Classified for ASJ and FSK; FHC 25/50 per ASTM E 84 for PSK;

meeting ASTM C 612 Type IA and IB; rigid.

- ‘K’ (‘SI’) Value: ASTM C 177, 0.23 at 75ºF (0.033 at 24ºC) mean temperature.

  - Maximum Service Temperature: 450ºF (232ºC).

  - Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type I, or FSK or PSK conforming to ASTM C 1136 Type II.

  - Verified formaldehyde free by UL Environment.

  - Securement: Secured in place using mechanical fasteners spaced a minimum of        12" (300 mm) on center with a minimum of 2 rows per side of duct.  Insulation shall be secured with speed washers and all joints, breaks and punctures sealed with appropriate pressure-sensitive foil tape, or glass fabric and vapor retarder mastic.

6.  Density:

a.	Concealed areas: Minimum 3 PCF (48 kg/m3).

b.	Exposed areas: Minimum 6 PCF (96 kg/m3).

E.	Outdoor Ductwork

- Aluminum Jacket: Shall be in thicknesses (smooth, corrugated, or embossed finish with factory applied moisture barrier) as specified in ASTM C 1729.  Overlap (both circumferential and longitudinal) shall be 2” (50 mm) minimum.

- PVC Jacket: Proto Corporation Indoor/Outdoor, UV resistant, white.  Closure shall be solvent weld adhesive or per manufacturer’s recommendations.

- Laminated Self-Adhesive Water and Weather Seals: applied per manufacturers’ recommendations.

- Glass Mineral Wool Duct Lining:  Knauf Sonic XP™ Duct Liner with ECOSE® Technology; conforming to ASTM C 1071 Type I and NFPA 90A & 90B; or Knauf Rigid Plenum Liner with ECOSE™ Technology complying with ASTM C 1071 Type II and NFPA 90A & 90B.

- UL/ULC Classified; UL GREENGUARD Certified.

- ‘K’ (‘SI’) Value: ASTM C 177, 0.24 at 75ºF (0.035 at 24ºC) mean temperature.

- Noise Reduction Coefficient (NRC): ASTM C 423 Type A Mounting, 0.45 or higher for ½" product, 0.70 or higher for 1" product.

- Maximum Air Velocity: 6000 FPM (1829 mpm) for Type I product, 5000 FPM 
(1524 mpm) for Type II product.

- Glass Mineral Wool Ductwork: Knauf Eclipse™ Air Duct Board with ECOSE® Technology,

UL Classified; conform to UL-181 Class 1 and NFPA 90A & 90B.

- ‘K’ (‘SI’) Value: ASTM C 177, 0.23 at 75ºF (0.033 at 24ºC) mean temperature.

- Maximum Temperature: 250°F (121°C).

- Maximum Internal Static Pressure: +/- 2" water gauge.

- Maximum Air Velocity: 5000 FPM (1524 mpm).

- Type shall be EI-475 with FSK facing.  In applications where additional rigidity is required, for large spans, where extra strength is needed, or where energy codes require R-6 or greater, type shall be EI-800.

2.4      MASTICS

A.    Vapor Retarder Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-900 ASJ or KI-905 ASJ+

2.  Water Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.04 perm (0.026 metric  
                       perm) at 40 mil dry film thickness.

3.  Service Temperature Range: -20°F to 120°F (-29°C to 82.2°C).

4.  Color: White

B.  Weather Barrier Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-700 ASJ or KI-705 ASJ+

2.  Water Vapor Permeance: ASTM F 1249, 1.8 perm (1.2 metric perm)

3.  Service Temperature: 0°F to 180°F constant (-17.8°C to 82.2°C); -20°F to 200°F 
                       intermittent (-29°C to 93°C)

4.  Solids: 58% by weight; 50% by volume

5.  Color: White

2.5      TAPES

A.    ASJ Tapes:

1.  Knauf Insulation EXPERT Tapes: ASJ Tape or ASJ+ Tape

2.  Width: 3 inches (75 mm) or 4 inches (101.6 mm)

3.  Thickness (Total): 14.3 mil (0.36 mm) – ASJ; 13.3 mil (0.34 mm) – ASJ+

4.  Adhesion: >4.8 Lbf / in. (840 N / m)

B.    FSK Tape:

1.  Knauf Insulation EXPERT Tapes: FSK Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 13.3 mil (0.34 mm)

4.  Adhesion: 6.5 Lbf / in. (1138 N / m)

C.   Aluminum Foil Tape:

1.  Knauf Insulation EXPERT Tapes: 2 Mil Foil Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 7.3 mil (0.19 mm)

4.  Adhesion: 4.0 Lbf / in. (700 N / m)

# PART 3—EXECUTION

3.1	EXAMINATION

- Verify that all piping, equipment, and ductwork are tested and approved prior to insulation installation.

- Verify that all surfaces are clean, dry and without foreign material before applying insulation

materials.

3.2	INSTALLATION

- All materials shall be installed by skilled labor regularly engaged in this type of work.  All materials shall be installed in strict accordance with manufacturer’s recommendations, building codes, and industry standards.

- Locate insulation and cover seams in the least visible location.  All surface finishes shall be extended in such a manner as to protect all raw edges, ends and surfaces of insulation.

- On cold surfaces where a vapor retarder must be maintained, insulation shall be applied with a continuous, unbroken moisture and vapor seal.  All hangers, supports, anchors, or other projections secured to cold surfaces shall be insulated and vapor sealed to prevent condensation.

- All pipe or duct insulation shall be continuous through walls, ceiling or floor openings, or sleeves except where firestop or firesafing materials are required.

- Piping Insulation – Glass Mineral Wool

- Locate all seams in water-shed location (10 o’clock / 2 o’clock or 8 o’clock / 4 o’clock).

- Insulation installed on piping operating below ambient temperatures must have a continuous vapor retarder. All joints, seams and fittings must be sealed.

- All ends must be firmly butted and secured with appropriate butt strip material. On high temperature piping, double layering with staggered joints may be appropriate.  When double layering, the inner layer should not be jacketed.

- Metal shields shall be installed between hangers or supports and the piping insulation. Rigid insulation inserts shall be installed as required between the pipe and the insulation shields. Inserts shall be of equal thickness to the adjacent insulation and shall be vapor sealed as required. Insulation inserts shall be no less than the following lengths:

1½" to 2½"  IPS		10" long

3" to 6"  IPS			12" long

8" to 10"  IPS			16" long

12" and over IPS		22" long

- For piping exposed in mechanical rooms or high traffic areas, insulation shall be protected from abuse by the use of appropriate thickness of PVC jacketing, metal jacketing, or laminated self-adhesive water and weather seal jacketing.

- For piping exposed to the elements, jacketing shall be Outdoor Weatherable PVC with a minimum thickness of 0.020 inches, or 0.016 inches thick aluminum or stainless steel with a factory applied moisture barrier, laminated self-adhesive water and weather seal jacket, or Redi-Klad® Pipe Insulation. Fitting covers shall be of similar materials. The insulation and jacketing shall be held firmly in place with a friction type Z lock or a minimum 2” overlap joint. All joints shall be sealed completely along the longitudinal seam and installed so as to shed water. All circumferential joints shall be sealed by use of preformed butt strips; minimum 2" wide or a minimum 2" overlap. Butt strips shall overlap the adjacent jacketing a minimum ½ inch and be completely weather sealed.  PVC Jacketing shall be limited to a maximum 20 inch OD of the insulation when exposed to direct sunlight. A 6" to 10" unsealed slide joint shall be installed every 25 to 30 lineal feet for the thermal expansion of the pipe and jacketing. In addition, a thin bead of silicone grease may be applied in the overlap to prevent water migration while allowing the joint to slide.  Where distance between fittings exceeds 8 lineal feet, an unsealed slide joint shall be installed. Insulation thickness for piping covered by PVC Jacketing shall be such that the surface temperature of the PVC does not exceed 125°F.

- Insulate valves, balancing valves and other devices requiring access with removable covers. Insulation shall have a minimum k-factor of .26 using glass mineral wool blanket. Flame spread and smoke developed shall be 25/50 per ASTM E-84. Covers shall be completely overlapping and completely cover the adjacent insulation. All seams and butt ends shall be secure.

- Cold Piping Insulation

  - On below freezing applications and in high abuse areas, the ASJ jacket shall be protected with a PVC vapor retarding outer jacket. In lieu of PVC, Knauf Redi-Klad® Pipe Insulation may be used. In addition, exposed ends of the insulation shall be sealed with a vapor retarder mastic installed per the manufacturer’s recommendations. Vapor seals at butt joints shall be applied at 12’ to 21’ intervals; at the Engineer’s discretion, and at each fitting to isolate any water incursion.

  - On chilled water systems operating in conditions of Design RH of 90% and above, it is recommended that the same guidelines be followed as listed above for below freezing applications.

- Piping Insulation: Pipe & Tank Insulations - Pipe & Tank Insulation or KwikFlex.

- Apply on clean, dry surfaces.

- Cut to appropriate length using manufacturers’ stretchout guide to for the specific pipe size. Add an additional 2” (51 mm) to 4” (102 mm) for a staple flap.

- Wrap around the pipe to ensure proper fit.

- Staple the lap on 3” (76 mm) centers with outward clinching staples.

- Ends shall be firmly butted and secured with matching butt strip material at each joint.

- On below ambient piping, vapor retarder mastic shall be applied to the ends at 12’ to 21’ intervals; at the Engineer’s discretion, and at each fitting before taping.

- Equipment Insulation – Glass Mineral Wool

- Apply insulation with joints firmly butted as close as possible to the equipment surface. Insulation shall be secured as required with mechanical fasteners or banding material. Fasteners shall be located a maximum of 3" from each edge and spaced no greater than 12" on center.

- Vapor retarders shall overlap a minimum of 2" at all seams and be sealed with appropriate pressure-sensitive tape or mastic. All penetrations, facing damage, and mechanical fasteners shall be covered with a minimum 2" overlap of tape or mastic.

- Equipment insulation exposed to the elements shall be finished with minimum 0.030” thick Outdoor Weatherable PVC, laminated self-adhesive water and weather seal jacket, weatherproof mastic and glass cloth, or metal. All joints shall be positioned so as to shed water; with a minimum 3" overlap, and completely weather sealed.

- For high temperature applications, insulation may be mounted against the hot surface, in H-bar configuration, or in panels mounted away from the operating surface. Insulation may be applied over welded pins or studs up to ½" in diameter. Insulation shall be held in place using mesh reinforcement or steel bands. Insulation shall not be compressed beyond a maximum of 5% at any point. Pins and studs shall be spaced a maximum of 4" from each edge and no greater than 16" on center. For temperatures above 550°F and design thicknesses over 3", insulation shall be applied double layer with staggered joints.  Finish shall be minimum 0.020” thick PVC Jacketing, insulating cement with canvas, glass cloth with mastic, or metal as specified on the drawings.

- For Equipment insulation exposed in mechanical rooms or subject to mechanical abuse, finish with minimum 0.020” thick PVC Jacketing or metal. All other insulation shall be finished as appropriate for the location and service or as specified on the drawings.

##### Internal Duct Lining – Glass Mineral Wool

- Duct Lining shall be applied in strict accordance with the latest edition of SMACNA’s “HVAC Duct Construction Standard Metal & Flexible” and NAIMA’s “Fibrous Glass Duct Liner Standard”.

- Length of mechanical fasteners shall be selected in accordance with the manufacturer’s recommendation as listed on each product.  Mechanical fasteners shall be installed perpendicular to the duct surface, and in no instance shall the pin compress the liner more than ⅛" relative to the nominal thickness of the insulation.

- Adhesive shall conform to ASTM C 916.  Adhesive shall be applied to the sheet metal with a 90% minimum coverage.  All exposed edges of the duct liner shall be coated with the same adhesive.  All rips and tears shall be repaired using an adhesive that conforms to ASTM C 916.

- All internal duct areas shall be covered with duct liner.  Transverse joints shall be firmly butted with no gaps and coated with adhesive.  Longitudinal corner joints shall be overlapped and compressed.

- When air velocities are 4000 to 6000 FPM, metal nosing shall be applied to all upstream transverse edges to additionally secure the insulation.

##### Flexible Glass Mineral Wool Blanket

- Install Duct Wrap to obtain specified R-value using a maximum compression of 25%.  Installed R-value shall be per ASHRAE 90.1-2010 or other design criteria.

- Firmly butt all joints.

- The longitudinal seam of the vapor retarder must be overlapped a minimum of 2”.          A 2” tab is provided on Knauf Friendly Feel( Duct Wrap for the circumferential seam.

- Where vapor retarder performance is required, all penetrations and damage to the facing shall be repaired using pressure-sensitive foil tape, or mastic prior to system startup.

- Pressure-sensitive foil tapes shall be a minimum 3” wide and shall be applied with moving pressure using a squeegee or other appropriate sealing tool.

- Closure shall have a 25/50 Flame Spread/Smoke Developed Rating per UL 723.

- Duct Wrap shall be additionally secured to the bottom of rectangular ductwork over 24” wide using mechanical fasteners on 18” centers.  Care should be exercised to avoid over-compression of the insulation during installation.

- Unfaced Duct Wrap shall be overlapped a minimum of 2” and fastened using 4” to 6” nails or skewers spaced 4” apart, or secured with a wire/banding system.  Care should be exercised to avoid damage to the Duct Wrap.

##### Round Ductwork: Pipe & Tank Insulation or KwikFlex.

- Apply on clean, dry surfaces.

- Cut to appropriate length using manufacturers’ stretchout guide to for the specific pipe size. Add an additional 2” (51 mm) to 4” (102 mm) for a staple flap.

- Wrap around the pipe to ensure proper fit.

- Staple the lap on 3” (76 mm) centers with outward clinching staples.  Ends shall be firmly butted and secured with matching butt strip material at each joint.

- On below ambient ductwork, appropriate UL approved vapor retarder shall be applied to all longitudinal and circumferential joints before application of butt strip material.

##### K.  Glass Mineral Wool Ductwork

- Ductwork shall be fabricated and installed in strict accordance with the latest edition NAIMA’s “Fibrous Glass Duct Construction Standard” and manufacturer’s recommendations.

- Closure system shall be UL 181 tested and listed:

  - Pressure-Sensitive Aluminum Foil Tapes: UL 181 Part I (marked UL 181 A-P).

  - Heat Sealable Closures: UL 181 Part II (marked UL 181 A-H).

  - Mastics: UL 181 Part III (marked UL 181 A-M) with 3” wide glass fabric.

- All longitudinal and transverse joints having a 1½" staple flap shall be secured with outward-cinching staples on approximate 2” centers and sealed with approved closure system.

- Transverse shiplap joints not having staples flaps, or transverse butt joints shall be secured with 8” long cross tabs running perpendicular to the joint seam on 12” centers.  Cross tabs shall be made from an approved closure tape.  The seam of the joint shall then be sealed with an approved closure system.

- Duct sections shall be additionally reinforced per NAIMA’s and manufacturer’s recommendations when necessary.  Reinforcement is dependent on duct width and operating pressure.

- Ductwork shall be suspended and supported as required on straight runs, at all turns, and at transitions to maintain proper alignment.  Hangers and supports shall be in strict accordance with NAIMA’s and manufacturer’s recommendations.

3.3	SCHEDULES

- ASHRAE 90.1-2010 Requirements, Pipe Insulation

1. The minimum insulation thicknesses based upon ASHRAE 90.1 do not 
     necessarily represent the Economic Thickness of Insulation or the 
     thickness required for proper condensation control. Rather, they serve 
     as minimum recommendations for commercial applications. For 
     recommended Economic Thickness and Systems Design, install 
     according to NAIMA ETI program (3E Plus) or as specified.

Minimum Pipe Insulation Thickness (in.)

Insulation Conductivity                                     Nominal Pipe or Tube Size (in.)

Fluid Design
Operating Temp.              Conductivity          Mean Rating            <1          1 to <1½       1½ to <4       4 to <8        ≥8
    Range (°F.)                 Btu∙in./(hr∙ft2∙°F)          Temp. °F.

Heating and Hot Water Systems (Steam, Steam Condensate, Hot Water Heating and Domestic Water Systems) a,b,c,d

>350                        0.32 – 0.34                  250                4.5             5.0              5.0             5.0         5.0
   251 – 350                   0.29 – 0.32                  200                3.0             4.0              4.5             4.5         4.5
   201 – 250                   0.27 – 0.30                  150                2.5             2.5              2.5             3.0         3.0
   141 – 200                   0.25 – 0.29                  125                1.5             1.5              2.0             2.0         2.0
   105 – 140                   0.22 – 0.28                  100                1.0             1.0              1.5             1.5         1.5

Cooling Systems (Chilled Water, Brine, and Refrigerant) a,b,f

40 – 60                     0.21 – 0.27                   75                0.5             0.5              1.0            1.0          1.0
        <40                        0.20 – 0.26                    50               0.5             1.0              1.0            1.0          1.5

a  For insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:

T = r[(1 + t/r)K/k - 1] where T = minimum insulation thickness (in,); r = actual outside radius of pipe (in).; t = insulation

thickness listed in this table for applicable fluid temperature and pipe size (in.); K = conductivity of alternate material

at the mean rating temperature indicated for the applicable fluid temperature  (Btu(in./[hr(ft2((F]); and k is the upper

value of the conductivity range listed in this table for the applicable fluid temperature.

b  These thicknesses are based on energy efficiency considerations only. Additional insulation is sometimes required

relative to safety issues/surface temperature. Issues such as water vapor permeability or surface condensation

sometimes require vapor retarders or additional insulation.

c	 For piping smaller than 1½”and located in partitions within conditioned spaces, reduction of these thicknesses by 1”

shall be permitted (before thickness adjustment required in footnote a) but not to thicknesses below 1”.

d	For direct-buried heating and hot water system piping, reduction of these thicknesses by 1.5” shall be permitted

(before thickness adjustment required in footnote a) but not to thicknesses below 1”.
e. The table is based on steel pipe. Non-metallic pipes schedule 80 thickness or less shall use the table thicknesses.

For other non-metallic pipes having thermal resistance greater than that of steel pipe, reduced insulation

thicknesses are permitted if documentation is provided showing that the pipe with the proposed insulation has no

more heat transfer per foot than the steel pipe of the same size with the insulation thickness shown on the table.

f. For direct-buried cooling system piping, insulation is not required.

- Necessary Pipe Insulation Thickness to Prevent Surface Condensation

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 80°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.5" | 1.0" | 1.0" |
| 1 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.5" | 1.5" | 1.0" |
| 1.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 1.5" | 1.5" | 1.5" |
| 2 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 1.5" | 1.5" | 1.5" |
| 4 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 2.0" | 1.5" | 1.5" |
| 6 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 8 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 10 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 12 | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 90°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 2.0" | 1.5" | 1.5" | 1.0" | 1.0" |
| 1 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 2.0" | 1.5" | 1.5" |
| 1.5 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 1.0" | 2.0" | 2.0" | 2.0" | 2.0" | 1.5" |
| 2 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 1.0" | 2.5" | 2.0" | 2.0" | 2.0" | 1.5" |
| 4 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 2.5" | 2.5" | 2.0" | 2.0" |
| 6 | 1.0" | 1.0" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 3.0" | 2.5" | 2.5" | 2.0" |
| 8 | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 3.0" | 2.5" | 2.5" | 2.0" |
| 10 | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.0" | 1.0" | 1.0" | 3.5" | 3.0" | 2.5" | 2.5" | 2.0" |
| 12 | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 1.5" | 1.5" | 1.0" | 1.0" | 1.0" | 3.5" | 3.0" | 2.5" | 2.5" | 2.0" |

C.         ASHRAE 90.1 – 2010 REQUIREMENTS – DUCT

Minimum Duct Insulation R-Value a, Cooling and Heating Only Supply Ducts and Return Ducts

Duct Location

Climate                        Ventilated    Unvented Attic     Unvented Attic    Unconditioned         Indirectly		    Buried
  Zone        Exterior         Attic	     Above Insulated	  with Roof	      Space b          Conditioned Space c
                                                               Ceiling		Insulation a

Heating – Only Ducts

1,2           none                none             none                      none                      none                       none                      none

3           R – 3.5             none             none                       none                     none                       none                      none

4           R – 3.5             none             none                       none                     none                       none                      none

5           R – 6.0            R – 3.5           none                      none                      none                       none                    R – 3.5

6           R – 6.0            R – 6.0          R – 3.5                    none                     none                       none                     R – 3.5

7           R – 8.0            R – 6.0          R – 6.0                    none                    R – 3.5                     none                    R – 3.5

8           R – 8.0            R – 8.0          R – 6.0                    none                    R – 6.0                     none                    R – 6.0

Cooling – Only Ducts

1            R – 6.0           R – 6.0          R – 8.0                  R – 3.5                  R – 3.5                     none                    R – 3.5

2            R – 6.0           R – 6.0          R – 6.0                  R – 3.5                  R – 3.5                     none                    R – 3.5

3            R – 6.0           R – 6.0          R – 6.0                  R – 3.5                  R – 1.9                     none                      none

4            R – 3.5           R – 3.5          R – 6.0                  R – 1.9                  R – 1.9                     none                      none

5,6           R – 3.5           R – 1.9          R – 3.5                  R – 1.9                  R – 1.9                     none                      none

7,8           R – 1.9           R – 1.9          R – 1.9                  R – 1.9                  R – 1.9                     none                      none

Return Ducts

1 to 8          R – 3.5           R – 3.5          R – 3.5                    none                     none                       none                      none

a Insulation R – values, measured in (hr∙ft2∙°F)/Btu, are for the insulation as installed and do not include film

resistance. The required minimum thicknesses do not consider water vapor transmission and possible surface

condensation. Where exterior walls are used as plenum walls, wall insulation shall be required by the most

restrictive conditions of Section 6.4.4.2 or Section 5. Insulation resistance measured on a horizontal plane in

accordance with ASTM C518 at a Mean temperature of 75° F at the installed thickness.

b Includes crawlspaces; both ventilated and non-ventilated.

c Includes return air plenum with or without exposed roofs above.

C.     (cont.)    ASHRAE 90.1 – 2010 REQUIREMENTS – DUCT

Minimum Duct Insulation R-Value a, Combined Heating and Cooling Supply Ducts and Return Ducts

Duct Location

Climate                        Ventilated    Unvented Attic     Unvented Attic    Unconditioned         Indirectly		    Buried
  Zone        Exterior         Attic	     Above Insulated	  with Roof	      Space b          Conditioned Space c
                                                               Ceiling		Insulation a

Supply Ducts

1            R – 6.0         R – 6.0           R – 8.0                  R – 3.5                   R – 3.5                    none                     R – 3.5

2            R – 6.0         R – 6.0           R – 6.0                  R – 3.5                   R – 3.5                    none                     R – 3.5

3            R – 6.0         R – 6.0           R – 6.0                  R – 3.5                   R – 3.5                    none                     R – 3.5

4            R – 6.0         R – 6.0           R – 6.0                  R – 3.5                   R – 3.5                    none                     R – 3.5

5            R – 6.0         R – 6.0           R – 6.0                  R – 1.9                   R – 3.5                    none                     R – 3.5

6            R – 8.0         R – 6.0           R – 6.0                  R – 1.9                   R – 3.5                    none                     R – 3.5

7            R – 8.0         R – 6.0           R – 6.0                  R – 1.9                   R – 3.5                    none                     R – 3.5

8            R – 8.0         R – 8.0           R – 8.0                  R – 1.9                   R – 6.0                    none                     R – 6.0

Return Ducts

1 to 8        R – 3.5          R – 3.5           R – 3.5                   none                      none                       none                       none

a Insulation R – values, measured in (hr∙ft2∙°F)/Btu, are for the insulation as installed and do not include film

resistance. The required minimum thicknesses do not consider water vapor transmission and possible surface

condensation. Where exterior walls are used as plenum walls, wall insulation shall be required by the most

restrictive conditions of Section 6.4.4.2 or Section 5. Insulation resistance measured on a horizontal plane in

accordance with ASTM C518 at a Mean temperature of 75° F at the installed thickness.

b Includes crawlspaces; both ventilated and non-ventilated.

c Includes return air plenum with or without exposed roofs above.

Minimum Duct Wrap R-Value (Installed) to Prevent Surface Condensation

| Jacket: Aged Aluminum Foil or Galvanized Sheet Metal (ε = 0.2) Wind Speed = 0 mph |
| --- |
| Operating Temperature: 45°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 2.2 | 3.3 | 4.3 | 4.3 | 5.4 |
| 70% | 3.3 | 5.4 | 6.5 | 7.6 | ** |
| 80% | 7.0 | ** | ** | ** | ** |
| Operating Temperature: 55°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 1.1 | 2.2 | 3.3 | 3.3 | 4.3 |
| 70% | 1.1 | 3.3 | 4.3 | 6.5 | 6.5 |
| 80% | 3.3 | 6.5 | ** | ** | ** |
| Operating Temperature: 65°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 1.1 | 1.1 | 2.2 | 3.3 | 4.3 |
| 70% | 1.1 | 1.1 | 3.3 | 5.4 | 6.5 |
| 80% | 2.2 | 3.3 | 6.5 | ** | ** |
| 90% | 6.5 | ** | ** | ** | ** |

** Necessary R-value is greater than one typically supplied in duct wrap.  Please consult manufacturer.

- Glass Mineral Wool Ductwork – Reinforcement Schedules

1.  Tie Rod System (Positive Pressure Only)

| Positive | Inside | TYPE 475 BOARD | TYPE 800 BOARD |
| --- | --- | --- | --- |
| Static Pressure | Duct Dimension (inches) | No. Rods Across Dimension | Maximum Longitudinal Spacing | No. Rods per 4 ft. Section | No. Rods Across Dimension | Maximum Longitudinal Spacing | No. Rods per 4 ft. Section |
|  | 0-36 |  | * |  |  | * |  |
|  | 37-42 | 2 | 24" | 4 | 2 |  | 2 |
| 0 thru ½" | 43-48 | 2 | 24" | 4 | 2 | 3 | 2 |
| W.G. | 49-60 | 3 | 24" | 6 | 3 | 3 | 3 |
|  | 61-64 | 3 | 24" | 6 | 3 | 24" | 6 |
|  | 65-80 | 4 | 24" | 8 | 4 | 24" | 8 |
|  | 81-96 | 5 | 24" | 10 | 5 | 24" | 10 |
|  | 0-24 |  | * |  |  | * |  |
|  | 25-30 | 1 | 24" | 2 | 1 | 48" | 1 |
| Over ½" | 31-32 | 1 | 24" | 2 | 1 | 24" | 2 |
| Thru 1" | 33-36 | 2 | 24" | 4 | 2 | 24" | 4 |
| W.G. | 37-48 | 2 | 24" | 4 | 2 | 24" | 4 |
|  | 49-64 | 3 | 24" | 6 | 3 | 24" | 6 |
|  | 65-80 | 4 | 24" | 8 | 4 | 24" | 8 |
|  | 81-96 | 5 | 24" | 10 | 5 | 24" | 10 |
|  | 0-15 |  | * |  |  | * |  |
|  | 16-18 | 1 | 24" | 2 |  | * |  |
|  | 19-24 | 1 | 24" | 2 | 1 | 24" | 2 |
| Over 1" | 25-32 | 1 | 16" | 3 | 1 | 24" | 2 |
| Thru 2" | 33-48 | 2 | 16" | 6 | 2 | 24" | 4 |
| W.G. | 49-60 | 3 | 16" | 9 | 3 | 24" | 6 |
|  | 61-64 | 3 | 16" | 9 | 3 | 16" | 9 |
|  | 65-80 | 4 | 16" | 12 | 4 | 16" | 12 |
|  | 81-96 | 5 | 16" | 15 | 5 | 16" | 15 |

*	Straight ducts of these dimensions do not require reinforcement.  However, some fittings of these 
    dimensions may require reinforcement.

NOTES:	1.	Tie rods and washers must be no more than 16" on center across duct dimension.

2.	Ducts of 48" width and over require use of anti-sag devices.

3.	For duct dimensions over 96", maintain tie rode spacing on 16 inch center across the duct  
    dimension following longitudinal spacing for the design pressure.

4.	If dimensions require, tie rods run in both horizontal and vertical directions.

2.   Channel System (Positive and Negative Pressure)

|  |  | Max. Inside | TYPE 475 BOARD | TYPE 800 BOARD |
| --- | --- | --- | --- | --- |
| Static Pressure |  | Duct Dimension (inches) | Maximum Longitudinal Spacing | Channel Gauge | H Dimension (see note) | Maximum Longitudinal Spacing | Channel Gauge | H Dimension (see note) |
| 0 thru ½" | negative | 0-30 |  | * |  |  | * |  |
| W.G. |  | 31-36 | 24" | 22 | 1" | 48" | 22 | 1" |
|  | positive | 0-36 |  | * |  |  | * |  |
|  |  | 37-42 | 24" | 22 | 1" | 48" | 22 | 1" |
| 0 thru ½" | positive | 43-48 | 24" | 22 | 1" | 48" | 22 | 1" |
| W.G. | or | 49-60 | 24" | 22 | 1" | 48" | 22 | 1½" |
|  | negative | 61-72 | 24" | 22 | 1" | 24" | 22 | 1" |
|  |  | 73-84 | 24" | 22 | 1" | 24" | 22 | 1" |
|  |  | 85-96 | 24" | 22 | 1¼" | 24" | 22 | 1" |
|  |  | 0-24 |  | * |  |  | * |  |
|  |  | 25-30 | 24" | 22 | 1" | 48" | 22 | 1" |
|  |  | 31-36 | 24" | 22 | 1" | 24" | 22 | 1" |
| Over ½" | positive | 37-42 | 24" | 22 | 1" | 24" | 22 | 1" |
| Thru 1" | or | 43-48 | 24" | 22 | 1" | 24" | 22 | 1" |
| W.G. | negative | 49-60 | 24" | 22 | 1" | 24" | 22 | 1" |
|  |  | 61-72 | 24" | 18 | 1" | 24" | 18 | 1" |
|  |  | 73-84 | 24" | 18 | 1¼" | 24" | 18 | 1¼" |
|  |  | 85-96 | 24" | 18 | 1¼" | 24" | 18 | 1¼" |
|  |  | 0-15 |  | * |  |  | * |  |
|  |  | 16-18 | 24" | 22 | 1" |  | * |  |
|  |  | 19-24 | 24" | 22 | 1" | 24" | 22 | 1" |
| Over 1" | positive | 25-36 | 16" | 22 | 1" | 24" | 22 | 1" |
| Thru 2" | or | 37-48 | 16" | 22 | 1" | 24" | 22 | 1¼" |
| W.G. | negative | 49-60 | 16" | 22 | 1" | 24" | 22 | 1¼" |
|  |  | 61-72 | 16" | 18 | 1" | 16" | 18 | 1" |
|  |  | 73-84 | 16" | 18 | 1¼" | 16" | 18 | 1¼" |
|  |  | 85-96 | 16" | 18 | 1½" | 16" | 18 | 1½" |

*	Straight ducts of these dimensions do not require reinforcement.  However, some fittings of these 
    dimensions may require reinforcement.

NOTES:	1.	Ducts of 48" width and over require use of anti-sag devices.

|  | H |  | GAUGE AS SPECIFIED |  |
| --- | --- | --- | --- | --- |
|  |  |  | 3" |  |

- Glass Mineral Wool Ductwork-Maximum Hanger Spacing

|  | Duct Size, Inches | Maximum Hanger Spacing |  |
| --- | --- | --- | --- |
|  | 48" wide or greater | 4 ft. |  |
|  | Less than 48" wide and less than 12" high | 6 ft. |  |
|  | Width between 24" & 48" and greater than 24" high | 6 ft. |  |
|  | Less than 48" wide and height between 12" & 24" | 8 ft. |  |
|  | Width 24" or less and height greater than 12" | 8 ft. |  |

END OF SECTION