# Updated 10-14-2014

# Table Of Contents

# SECTION 220700 – PLUMBING INSULATION

# PART 1 — GENERAL

1.1     RELATED DOCUMENTS

1.2     SUMMARY

1.3     SUBMITTALS FOR INFORMATION

1.4     QUALITY ASSURANCE

# PART 2 — PRODUCTS

2.1     INSULATION MATERIALS

2.2     FACTORY APPLIED JACKETS

2.3     FIELD APPLIED JACKETS

# PART 3 — EXECUTION

3.1	EXAMINATION

3.2	GENERAL INSULATION REQUIREMENTS

3.3	PIPING INSULATION

3.4	PIPING INSULATION: PIPE & TANK INSULATION AND KWIKFLEX™

3.5	EQUIPMENT INSULATION – GLASS MINERAL WOOL

3.6	INSULATION SCHEDULES

# SECTION 220700 – PLUMBING INSULATION

# PART 1 — GENERAL

# 1.1     RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specifications, apply to this Section.

# 1.2     SUMMARY

A.	Section Includes:

1.	Insulation Materials:

a.	Piping insulation, jacketing and accessories

b.	Equipment insulation and jacketing or coatings

c.	Mastics and Tapes

d.	Laminated self-adhesive water and weather seal such as VentureClad

e.	PVC fittings and inserts

f.	Pre-formed; formaldehyde free glass mineral wool fittings

2.	References

a.	ASTM International (ASTM)

b.	American Society of Heating, Refrigerating, and Air Conditioning Engineers, Inc. (ASHRAE)

c.	North American Insulation Manufacturers Association (NAIMA)

d.	National Fire Protection Association (NFPA)

e.	Sheet Metal and Air Conditioning Contractors National Association, Inc. (SMACNA)

f.	Underwriter’s Laboratories (UL)

g.	Underwriter’s Laboratories Environment (UL Environment )

3.	Definitions

a.	Thermal Conductivity (k value): Btu•in./hr.•ft²•°F

b.	UL GREENGUARD provides independent, third-party, Indoor Air Quality (IAQ) certification of products for emissions of respirable particles and Volatile Organic Compounds (VOC’s), including formaldehyde and other specific product-related pollutants. Certification is based upon criteria used by EPA, OSHA and WHO.

c.	IAQ: Indoor Air Quality

d.	EPA: Environmental Protection Agency

e.	WHO: World Health Organization

f.	ASJ+: All Service Jacket composed of aluminum foil reinforced with glass scrim bonded to a kraft paper interleaving with an outer film layer leaving no paper exposed.

g.	ASJ: All Service Jacket

h.	SSL+: Self-sealing Advanced Closure System

i.	SSL: Self-Sealing Lap

j.	FSK: Foil Scrim Kraft; jacketing

k.	PSK: Poly Scrim Kraft; jacketing

l.	PVC: Polyvinyl Chloride

m.    FRP: Fiberglass Reinforced Plastic

n.     Glass MINERAL Wool: Interchangeable with fiber glass, but replacing the term with   
                                   the intent to disassociate and differentiate Glass Mineral Wool from the potential 
                                   health and safety risk of special purpose or reinforcement products that do not meet  
                                   the bio soluble criteria of insulation made from glass.

o.     ECOSE® Technology: a revolutionary new binder system based on rapidly renewable 	 	         bio-based materials rather than petroleum-based chemicals commonly used in other             		         glass mineral wool insulation products. ECOSE Technology reduces the binder

embodied energy by up to 70% and does not contain phenol, formaldehyde, acrylics

or artificial colors.

p.      UL GREENGUARD Gold Certification: (Formerly known as 
                                   GREENGUARD Children & Schools Certification) offers stricter certification 
                                   criteria, considers safety factors to account for sensitive individuals (such as children 
                                   and the elderly), and ensures that a product is acceptable for use in environments 
                                   such as schools and healthcare facilities. It is referenced by, both The Collaborative 
                                   for High Performance Schools (CHPS) and the Leadership in Energy and 
                                   Environmental Design (LEED) Building Rating Systems.

q.       UL Environment Formaldehyde Free Verification Requirements: for

a product to be verified as formaldehyde free, product samples must have a

measured emission factor of less than or equal to 5 µg/m2 h at 24 elapsed hours or

3 µg/m2 h at 336 elapsed hours. An emission factor of 5 µg/m2 h, corresponds to a

measured chamber concentration of 2.5 µg/m3 for a typical building ratio of 0.5 m2/m3.

This chamber concentration is comparable to, or below typical outdoor air

concentrations. This demonstrates that the formaldehyde exposure from products

labeled as formaldehyde free will not contribute to airborne formaldehyde

concentrations at greater levels than those found in the natural outdoor environment.

r.       Declare and The Living Building Challenge – The Living Building Challenge is a

philosophy, advocacy tool and certification program that addresses development at

all scales. The purpose of The Living Building Challenge is to define the most

advanced measure of sustainability in the built environment today and acts to

diminish the gap between current limits and ideal solutions. Declare supports The

Living Building Challenge by providing a transparent materials database that project

teams can select from to meet Imperative 11.

s.       Imperative 11, Red List – requires that manufacturers disclose the ingredients in their

products to insure that they are free of Red List chemicals and materials. The Red

List represents the “worst in class” materials, chemicals and elements known to pose

serious risks to human health and the greater ecosystem.

t.       Underwriter’s Laboratories Environment (UL Environment): offers

independent green claims validation, product assessment and certification.

UL GREENGUARD provides third-party credibility for sustainable

products.

u.      UL Environment Claims Validation (ECV): service and label tests a manufacturer’s

product and validates that the environmental claims they make in their marketing and

packaging materials are factual. This Environmental Claims Validation (ECV) service

will allow manufacturers to verify that their products contain a quantifiable amount of

recycled content and, as such, help limit raw material extraction and reduce landfill

waste. It also will enable products to qualify for LEED® points under

Pilot Credit 43: MR – Certified Products.

v.       EUCEB: exonerated fiber from a health and safety standpoint by the European

Certification Board process.

w.      Recycled content – Post-Consumer: materials such as bottled glass collected at

curbside or other collection sites after consumer use and used in the manufacturing

process to create a new product rather than being placed in a landfill or incinerated.

x.      Recycled content – Pre-Consumer (aka post-industrial): materials used or created

from one manufacturing process which are collected as scrap and placed back into

another manufacturing process rather than being placed in a landfill or incinerated.

y.      Polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or

Deca-BDE fire retardants: have been linked to adverse health effects after exposure

in low concentrations.

z.      UL Classified: UL has tested and evaluated samples of the product with respect to

certain properties of the product. UL Classifies products to:

Applicable UL requirements

Standards for safety

Standards of other National and International organizations

aa.    EPD: Environmental Product Declaration. A third party verified document that reports  
         environmental data of products based on the Life Cycle Assessment (LCA) and other

relevant information, and in accordance with the International Standard ISO 14025

(Type III Environmental Declarations)

B.	Related Sections:

1.	Division 23 Section "HVAC Insulation"

# 1.3     SUBMITTALS FOR INFORMATION

A.	Product data: To include product description, manufacturer's installation instructions, and   appropriate specification compliance. Thickness is determined by Engineer and provided in a thickness schedule. Locations are dictated by project design.

B.	Samples and mockups of systems shall be provided upon engineer’s request.

C.	EPD Submittals: As certified by UL Environment

D.     LEED Submittals:

1.	Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including   
printed statement of VOC content and chemical components.

2.	Product Data for Credit MR 5 Regional Materials: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

3.	LEED v 4, Product Data for Credit EA 2: For products and materials significant to the energy performance of a structure, provide documentation that indicates that insulation levels are significant to increasing the level of energy performance beyond the prerequisite standard.

4.	LEED v 4, Product Data for Credit MR 2: For products and materials to comply with Building Product Disclosure & Optimization, provide data/evidence that substantiates Environmental Product Declaration and Multi Attribute Optimization requirements.

5.	LEED v 4: Product Data for Credit MR 3: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

6.	LEED v 4, Product Data for Credit MR 4: For products having recycled content documentation; indicating percentages by weight of post-consumer and pre-consumer recycled content. Include statement indicating cost for each product having recycled content.

7.	LEED v 4, Product Data for Credit EQ 2:  For products and materials to comply with low emittance standards, provide documentation substantiating that insulation products comply with requisite low emittance standards.

8.	LEED v 4, Product Data for Credit EQ 5: For products and materials to meet the standard for both thermal comfort design and thermal comfort control, provide data to support that insulation products are significant to thermal comfort design and thermal comfort control.

9.	LEED v 4, Product Data for Credit EQ 9: For products and materials that contribute to the design and performance of workspaces that promote occupants well-being, productivity, and communication, provide data/documentation supporting acoustical benefits of Glass Mineral Wool insulation products.

10.	Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that product complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small Scale Environmental Chambers."

# 1.4     QUALITY ASSURANCE

A.	Surface Burning Characteristics: Insulation and related materials shall have surface burning            characteristics determined by test performed on identical products per UL 723 or ASTM E 84 mounted and installed as per ASTM E 2231. All testing shall be performed by a testing and inspecting agency acceptable to authorities having jurisdiction. Insulation, jacket materials, adhesives, mastics, tapes and cement material containers shall be labeled with appropriate markings of applicable testing and inspecting agency.

1.	Insulation installed indoors:  Flame spread index of 25 or less, and smoke developed index of 50 or less.

2.	Insulation installed outdoors:  Flame spread index of 75 or less, and smoke developed index of 150 or less.

B.	Store tapes, adhesives, mastics, cements, and insulation materials in ambient conditions in accordance with the recommendations of the manufacturer.

C.	Follow manufacturer’s recommended handling practices.

D.    Supply glass mineral wool insulation products that are manufactured using a minimum of 50% “post-consumer” recycled material.

E.	Supply glass mineral wool insulation products that are manufactured using a bio-based binder rather than non-renewable petroleum-based chemicals and with a binder that does not contain phenol, formaldehyde, or acrylics; whenever possible.

F.	Supply glass mineral wool insulation products that have achieved UL GREENGUARD Gold Certification and are verified formaldehyde free by UL Environment; whenever possible.

G.    Supply glass mineral wool insulation products that are Living Building Challenge – Declare, Red List free; whenever possible.

H.    Products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE,

Octa-BDE or Deca-BDE fire retardants; whenever available.

I.	WET: Contractor shall take precaution to protect insulation materials from moisture exposure or physical damage. Any glass mineral wool insulation that becomes wet or damaged shall be replaced at no additional cost.

1.  HVAC duct work insulation used in the air stream must be discarded if exposed to

liquid water.

2.  Pipe Insulation with factory applied ASJ+ facing having been installed per

manufacturer’s installation recommendation which may experience intermittent exposure to

liquid water after installation may be exempted from removal and replacement requirements.

# PART 2 — PRODUCTS

# 2.1     INSULATION MATERIALS

A.	Insulation products shall not contain asbestos, lead, mercury, mercury compounds, or formaldehyde. Products shall be certified by UL GREENGUARD GOLD or Indoor Advantage Gold.

B.	Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

C.    Insulation materials applied to carbon steel shall be Mass Load Corrosion Rate (MLCR) tested per ASTM C 1617.

D.	Manufacturers: Knauf Insulation, Proto Corporation, ICA Hamfab, VentureClad, or pre-approved substitute.

E.	Glass Mineral Wool: Knauf Insulation Earthwool™ 1000( Pipe Insulation with ECOSE® Technology, UL/ULC Classified, EPD Certified by UL Environment, Living Building Challenge – Declare, Red List free for unjacketed Pipe, meeting ASTM C 547 Type IV Grade A, ASTM C 585, ASTM C411 and ASTM C 795; rigid, molded, k value: ASTM C 335, 0.23 at 75(F (0.033 at 24(C) mean temperature. Maximum Service Temperature: 1000(F (538(C). Vapor Retarder Jacket: ASJ+/SSL+ conforming to  ASTM C 1136 Type I, II, III, IV, & VIII secured with self-sealing longitudinal laps and matching ASJ+ butt strips. Verified to be formaldehyde free by

UL Environment.

F.	Glass Mineral Wool: Knauf Insulation Earthwool™ Redi-Klad® 1000° Pipe Insulation with ECOSE® Technology, Component FHC 25/50 per ASTM E 84, EPD Certified by UL Environment, Living Building Challenge – Declare, Red List free, meeting ASTM C 547 Type IV Grade A, ASTM C 585, ASTM C411 and ASTM C 795; rigid, molded; k value: ASTM C 335, 0.23 at 75( F (0.033 at 24( C) mean temperature. Maximum Service Temperature: 1000( F (538( C). Redi-Klad Jacket: VentureClad 5-ply weather and abuse resistant with self-seal lap. Zero permeability per ASTM E 96-05; puncture resistance 35.4 kg (189.3 N) per ASTM D 1000; tear strength 4.3 lb. (19.4 N) per ASTM D 624; thickness 14.5 mils (0.0145"); tensile strength

68.0 lb./inch width [306 N (31 kg)/25 mm].

G.	Glass Mineral Wool: Knauf Pipe & Tank Insulation with ECOSE® Technology; semi-rigid, limited combustible meeting requirements of ASTM C 1393; NRC 1.36; ASTM C 795, ASTM C447 and MIL-I-24244C. k value: ASTM C 177, 0.25 at 75( F (0.036 at 24(C) mean temperature. Maximum Service Temperature: 850(F (454(C). Compressive Strength: not less than 120 PSF (5.75 kPa) @ 10% deformation per ASTM C 165. Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type II, FHC 25/50 per ASTM E 84.

H.	Glass Mineral Wool: Knauf KwikFlex™; semi-rigid glass mineral wool blanket in roll form , UL/ULC Classified ASJ and FSK; FHC 25/50 per ASTM E 84 PSK only; meeting requirements of UL 723, ASTM C 1393, ASTM C447 and  ASTM C 356. k value: ASTM C 518, 0.24 at 75( F (0.035 at 24(C) mean temperature. Maximum Service Temperature: 850(F (454(C); maximum surface temperature for faced product: 150( F (66( C); maximum thickness @ 850( F:  4 inches

(102 mm). Compressive Strength: not less than 25 PSF (1.2 kPa) @ 10% deformation per        ASTM C 165. Vapor Retarder Jacket:  ASJ, FSK or PSK conforming to ASTM E 96,

Procedure A.

I.	Fitting Insulation: Insulate using pre-formed PVC fitting covers with glass mineral wool inserts. Alternatively, preformed molded, formaldehyde free glass mineral wool; minimum 50% post-consumer recycled glass content, or mitered glass mineral wool pipe insulation sections. These fittings shall be further protected by field-applied PVC fitting covers, metal fitting covers, or glass fabric and mastic sealed as necessary.

# 2.2     FACTORY APPLIED JACKETS

A.     ASJ+/SSL+:  All service jacket with Advanced Closure System self-sealing lap. All Service Jacket composed of aluminum foil reinforced with glass scrim bonded to a kraft paper interleaving with an outer film layer leaving no paper exposed.; conforming to ASTM C 1136 Type I, II, III, IV, and VIII; vapor retarder; with a self-sealing adhesive.

B.	ASJ: All service jacket. White kraft paper bonded to aluminum foil and reinforced with glass fibers; conforming to ASTM C 1136; vapor retarder.

C.	FSK: Foil scrim kraft. Aluminum foil, fiberglass reinforced scrim with kraft backing; conforming to ASTM C 1136 Type 1; vapor retarder.

D.	PSK: Poly scrim kraft. Metalized polypropylene, fiberglass reinforced scrim with kraft backing; conforming to ASTM C 1136 Type 1; vapor retarder.

E.	Redi-Klad Jacket: VentureClad 5-ply weather and abuse resistant with self-seal lap,

Living Building Challenge – Declare, Red List free.  Zero permeability per ASTM E 96-05; puncture resistance 35.4 kg (189.3 N) per ASTM D 1000; tear strength 4.3 lb. (19.4 N) per ASTM D 624; thickness 14.5 mils (0.0145"); tensile strength 68.0 lb./inch width

[306 N (31 kg)/25 mm].

F.     Fire Retardant: products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE; whenever available.

# 2.3     FIELD APPLIED JACKETS

A.	PVC: Proto Corporation 25/50 or Indoor/Outdoor, UV resistant fittings, jacketing and accessories, white or colored. Fitting cover system consists of pre-molded, high-impact PVC materials with glass mineral wool inserts. Glass mineral wool insert has a thermal conductivity (k value) of 0.26 at 75( F (0.037 at 24(C) mean temperature. Closures: stainless steel tacks, matching PVC tape, or PVC adhesive per manufacturer’s recommendations.

B.	Aluminum Jacket: Alloy 3003 or 3105, minimum thickness per ASTM C 1729, smooth, corrugated or stucco embossed with factory-applied moisture barrier. Overlap shall be 2 inch (50 mm) minimum. Jacket shall be banded in place with ½” x 0.20” aluminum strapping fastened with aluminum wing seals.

C.    Stainless Steel Jacket: T-304, minimum per ASTM C 1729, smooth, corrugated or embossed with factory-applied moisture barrier. Overlap shall be 2 inch (50 mm) minimum. Jacket shall be banded in place with ⅜” x 0.20” aluminum strapping fastened with stainless steel wing seals.

D.	Laminated Self-Adhesive Water and Weather Seals: permanent acrylic self-adhesive system; weather resistant, high puncture and tear resistance; meeting or exceeding requirements of

UL 723; and applied in strict accordance with manufacturers’ recommendations.

E.     Fire Retardant: products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE; whenever available.

2.4      MASTICS

A.    Vapor Retarder Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-900 ASJ or KI-905 ASJ+

2.  Water Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.04 perm (0.026 metric perm) at 
                       40 mil dry film thickness.

3.  Service Temperature Range: -20°F to 180°F (-29°C to 82.2°C).

4.  Color: White

B.  Weather Barrier Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-700 ASJ or KI-705 ASJ+

2.  Water Vapor Permeance: ASTM F 1249, 1.8 perm (1.2 metric perm)

3.  Service Temperature: 0°F to 180°F constant (-17.8°C to 82.2°C); -20°F to 200°F intermittent
                       (-29°C to 93°C)

4.  Solids: 58% by weight; 50% by volume

5.  Color: White

2.5      TAPES

A.    ASJ Tapes:

1.  Knauf Insulation EXPERT Tapes: ASJ Tape or ASJ+ Tape

2.  Width: 3 inches (75 mm) or 4 inches (101.6 mm)

3.  Thickness (Total): 14.3 mil (0.36 mm) – ASJ; 13.3 mil (0.34 mm) – ASJ+

4.  Adhesion: >4.8 Lbf / in. (840 N / m)

B.    FSK Tape:

1.  Knauf Insulation EXPERT Tapes: FSK Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 13.3 mil (0.34 mm)

4.  Adhesion: 6.5 Lbf / in. (1138 N / m)

C.   Aluminum Foil Tape:

1.  Knauf Insulation EXPERT Tapes: 2 Mil Foil Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 7.3 mil (0.19 mm)

4.  Adhesion: 4.0 Lbf / in. (700 N / m)

# PART 3 — EXECUTION

3.1      EXAMINATION

A.	Verify that all piping and equipment are tested and approved prior to insulation installation.

B.	Verify that all surfaces are clean, dry and without foreign material before applying insulation materials.

3.2     GENERAL INSULATION REQUIREMENTS

A.	All materials shall be installed by skilled labor regularly engaged in this type of work.  All materials shall be installed in strict accordance with manufacturer’s recommendations, building codes, and industry standards.

B.	Locate insulation and cover seams in the least visible location.  All surface finishes shall be extended in such a manner as to protect all raw edges, ends and surfaces of insulation.

C.	On cold surfaces where a vapor seal must be maintained, insulation shall be applied with a continuous, unbroken moisture and vapor retarder.  All hangers, supports, anchors, or other projections secured to cold surfaces shall be insulated and vapor sealed to prevent condensation.

D.	All pipe insulation shall be continuous through walls, ceiling or floor openings, or sleeves except where firestop or firesafing materials are required.

E.	Install multiple layers of insulation with longitudinal and circumferential joints staggered.

3.3     PIPING INSULATION: 1000° PIPE INSULATION AND REDI-KLAD PIPE INSULATION

A.	Locate longitudinal pipe insulation jacketing laps in the least visible location.

B.	Longitudinal jacketing lap joints for pipe insulation installed on piping systems with operating temperatures below ambient shall be vapor sealed with factory-applied pressure sensitive adhesive, vapor retarder self-sealing lap. For proper sealing, lap joints shall be sealed with reasonable pressure being applied with a plastic squeegee. All circumferential joints shall be vapor sealed with factory furnished matching, pressure sensitive butt strips installed with reasonable pressure being applied with a plastic squeegee. Additionally, raw ends of pipe insulation sections shall be coated with vapor retarder mastic at 12’ to 21’ intervals; at the Engineer’s discretion on straight piping and on either side of all fittings, flanges or valves. Vapor retarder mastic shall completely coat the ends of the pipe insulation and extend onto the bore of the pipe insulation and onto the jacketing a minimum of 2”.

C.	On high temperature piping, above 500°F (260°C), insulation shall be applied using double layer with staggered joints. When double layering, the inner layer should not be jacketed. All joints and ends must be firmly butted and secured with appropriate securement material.

D.	Metal shields shall be installed between hangers or supports and the piping insulation. Rigid insulation inserts shall be installed as required between the pipe and the insulation shields. Inserts shall be of equal thickness to the adjacent insulation and shall be vapor sealed as required. Insulation inserts shall be no less than the following lengths:

1½" to 2½″ IPS	10″ long

3″ to 6″ IPS	12″ long

8″ to 10″ IPS	16″ long

12″ and over IPS	22″ long

E.	For piping exposed in mechanical rooms or high traffic areas, insulation shall be protected from abuse by the use of appropriate thickness of PVC jacketing, metal jacketing or laminated

self-adhesive water and weather seals.

F.	For piping exposed to the elements install Redi-Klad with 4″ butt strips and self sealing lap or a jacketing that shall be UV resistant PVC with a minimum thickness of 0.020 inches, or 0.016 inches (0.406) thick aluminum with factory applied moisture barrier or 0.010 inches (0.254mm) thick stainless steel with a factory applied moisture barrier. Fitting covers shall be of similar materials. The insulation and jacketing shall be held firmly in place with a friction type Z lock or a minimum 2″ overlap joint. For systems operating below ambient, all PVC joints shall be sealed completely along the longitudinal and circumferential seams and installed so as to shed water. When required, all PVC circumferential joints shall be sealed by use of preformed butt strips; minimum 2″ wide or a minimum 2″ overlap. Butt strips shall overlap the adjacent jacketing a minimum ½ inch and be completely weather sealed. PVC Jacketing shall be limited to a maximum 20 inch OD of the insulation when exposed to direct sunlight. For systems operating above ambient, circumferential joints should overlap a minimum of 2″ and not be sealed. Insulation thickness for piping covered by PVC Jacketing shall be such that the surface temperature of the PVC does not exceed 125(F (52(C).

G.    Insulate valves, balancing valves and other devices requiring access with removable covers. Covers shall have a minimum k-factor of .26; using glass mineral wool blanket. Flame spread and smoke developed shall be 25/50 per ASTM E-84. Covers shall be completely overlapping and completely cover the adjacent insulation with seams and butt ends secure.

H.	Cold Piping Installation / High Abuse Systems

1.	On systems operating below freezing or systems operating in high abuse areas install Redi-Klad with 4″ butt strips and self sealing lap; or the ASJ+ jacket shall be protected with a PVC vapor retarding outer jacket. In addition, exposed ends of the insulation shall be sealed with a vapor retarder mastic installed per the manufacturer’s recommendations. Vapor stops: vapor retarder mastic applied in the insulation butt joint from the vapor retarder jacket to the bore of the pipe; a minimum of 2”, shall be applied at 12’ to 21’ intervals; at the Engineer’s discretion, and at each fitting to isolate any water incursion or transmission.

2.	On systems operating below ambient and in conditions of Design RH of 90% and above, it is recommended that the same guidelines be followed as listed above for below freezing applications.

3.4	PIPING INSULATION: PIPE & TANK INSULATION AND KWIKFLEX

A.	Apply on clean, dry surfaces.

B.	Cut to appropriate length using manufacturers’ stretchout guide for the specific pipe size. Add an additional 2 inches (51 mm) to 4 inches (102 mm) for a staple flap.

C.	Install insulation around the pipe circumference in a manner that ensures a firm fiber mesh at all joints. Fasten the longitudinal with outward clinching staples placed 3 inches on center      (76 mm). As an alternative, individual sections may be fastened in place using continuous and overlapping strands of ¾” wide glass fiber filament tape around the insulation jacketing O.D. Longitudinal and circumferential joints shall be sealed with 4” wide matching pressure sensitive tape squeegeed along the entire length.

D.	For piping exposed to the elements, jacketing shall be UV resistant PVC with a minimum thickness of 0.020 inches, or 0.016 inches (0.406) thick aluminum with factory applied moisture barrier or 0.010 inches (0.254mm) thick stainless steel with a factory applied moisture barrier or laminated self-adhesive water and weather seals. Fitting covers shall be of similar materials. The insulation and jacketing shall be held firmly in place with a friction type Z lock or a minimum 2″ overlap joint. For systems operating below ambient, all PVC joints shall be sealed completely along the longitudinal and circumferential seams and installed so as to shed water. When required, all PVC circumferential joints shall be sealed by use of preformed butt strips; minimum 2″ wide or a minimum 2″ overlap. Butt strips shall overlap the adjacent jacketing a minimum ½ inch and be completely weather sealed. PVC Jacketing shall be limited to a maximum 20 inch OD of the insulation when exposed to direct sunlight. For systems operating above ambient, circumferential joints should overlap a minimum of 2″ and not be sealed. Insulation thickness for piping covered by PVC Jacketing shall be such that the surface temperature of the PVC does not exceed 125(F (52(C).

E.    On below ambient straight piping, vapor retarder mastic shall be applied to raw glass fiber ends at 12’ to 21’  intervals; at the Engineer’s discretion, and on either side of fittings, flanges or valves before taping. Mastic shall extend a minimum of 2 inches onto the bore of the pipe and 2 inches onto the jacketing.

3.5     EQUIPMENT INSULATION - GLASS MINERAL WOOL

A.	Apply insulation to the equipment surface with joints firmly butted and as close as possible to the equipment surface. Insulation shall be secured as required with mechanical fasteners or banding material. Fasteners shall be located a maximum of 3″ from each edge and spaced no greater than 12″ on center.

B.	For below ambient systems, vapor retarder jacketing shall overlap a minimum of 2″ at all seams and be sealed with appropriate pressure-sensitive tape or mastic. All penetrations and facing damage shall be covered with a minimum 2″ (51mm) overlap of tape or mastic.

C.	Equipment insulation exposed to the elements shall be finished with minimum 0.030 inch thick, outdoor, weather resistant PVC; laminated self-adhesive water and weather seal material; or metal. All longitudinal joints shall be positioned so as to shed water; with a minimum 3″ overlap, and completely weather sealed. Laminated systems shall be applied per manufacturer’s recommendations.

D.	For high temperature applications, insulation may either be mounted in direct contact with the hot surface, in H-bar configuration, or pre-fabricated panel systems mounted away from the operating surface. When installing H-Bar or panel systems which are mounted away from the operating surface, convection stops shall be installed at a maximum of 8 feet along the vertical surfaces. Insulation may be applied over welded pins or studs up to ½″ in diameter. Insulation shall be held in place using mesh reinforcement or steel bands. Insulation shall not be compressed beyond a maximum of 1/8 inch at any point. Pins and studs shall be spaced a maximum of 4″ from each edge and no greater than 16″ on center. For temperatures above 500(F (260°C) and design thicknesses over 3″, insulation shall be applied using double layer with staggered joints.  Finish shall be minimum 0.020 inch thick PVC jacketing, insulating cement with canvas, glass cloth with mastic, or metal as specified on the drawings.

E.	For Equipment insulation exposed in mechanical rooms or subject to mechanical abuse, finish with minimum 0.020 inch thick PVC jacketing or metal or laminated self-adhesive water and weather seal material. All other insulation shall be finished as appropriate for the location and service or as specified on the drawings.

  - INSULATION SCHEDULES

- ASHRAE 90.1 – 2010 Requirements, Pipe Insulation

  - The minimum insulation thickness based upon ASHRAE 90.1 do not necessarily

represent the Economic Thickness of Insulation or the thickness required for

proper condensation control. Rather, they serve as minimum recommendations for

commercial applications. For recommended Economic Thickness and System Design,

install according to NAIMA 3E Plus or as specified.

# Minimum Pipe Insulation Thickness

Insulation Conductivity                                     Nominal Pipe or Tube Size (in.)

# Fluid Design

Operating Temp.            Conductivity               Mean Rating          <1         1 to < 1½       1½ to < 4       4 to <8         ≥8

Range (° F.)              Btu·in./(hr·ft²·°F)               Temp. °F.

# Heating and Hot Water Systems- Steam, Steam Condensate, Hot Water Heating and Domestic Water Systemsa,b,c,d

>350			0.32 – 0.34	           250	       4.5            5.0              5.0              5.0          5.0

251 – 350		0.29 – 0.32                   200                3.0            4.0              4.5              4.5          4.5

201 – 250                  0.27 – 0.30                   150                2.5            2.5              3.0              3.0          3.0

141 – 200                  0.25 – 0.29                   125                1.5            1.5              2.0              2.0          2.0

105 – 140                  0.22 – 0.28                   100                1.0            1.0              1.5              1.5          1.5

# Cooling Systems (Chilled Water, Brine, and Refrigerant) a,b,f

40 – 60                  0.21 – 0.27                    100               0.5            0.5              1.0               1.0          1.0

<40                     0.20 – 0.26                    100               0.5            1.0              1.0               1.0          1.5

a For insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:

# T = r{(1 + t/r)K/k – 1} where T = minimum insulation thickness (in.), r = actual outside radius of pipe (in.), t = insulation

# thickness listed in this table for applicable fluid temperature and pipe size, K = conductivity of alternate material at mean

# rating temperature indicated for the applicable fluid temperature (Btu·in.[hr·ft²·°F]), and k = the upper value of the

# conductivity range listed in this table for the applicable fluid temperature.

b These thicknesses are based on energy efficiency considerations only. Additional insulation is sometimes required

relative to safety issues/surface temperature. Issues such as water vapor permeability or surface condensation

sometimes require vapor retarders or additional insulation.

c For piping smaller than 1½” and located in partitions within conditioned spaces, reduction of these thicknesses by 1”

shall be permitted (before the thickness adjustment required in footnote a) but not to thicknesses below 1”.

d For direct-buried heating and hot water system piping, reduction of these thicknesses by 1.5” shall be permitted (before

thickness adjustment required in footnote a) but not to thicknesses below 1”.

e The table is based on steel pipe. Non-metallic pipes schedule 80 thickness or less shall use the table

values. For other non-metallic pipes having thermal resistance greater than that of steel pipe, reduced

thicknesses are permitted if documentation is provided showing that the pipe with the proposed insulation

has no more heat transfer per foot than a steel pipe of the same size with the insulation thickness shown on

the table.

f  For direct-buried cooling system piping, insulation is not required.

- NECESSARY PIPE INSULATION THICKNESS TO PREVENT CONDENSATION:

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 80°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.5" | 1.0" | 1.0" |
| 1 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.5" | 1.5" | 1.0" |
| 1.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 1.5" | 1.5" | 1.5" |
| 2 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 1.5" | 1.5" | 1.5" |
| 4 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 2.0" | 1.5" | 1.5" |
| 6 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 8 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 10 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 0.5" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |
| 12 | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 2.5" | 2.5" | 2.0" | 2.0" | 1.5" |

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 90°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 2.0" | 1.5" | 1.5" | 1.0" | 1.0" |
| 1 | 0.5" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 2.0" | 2.0" | 2.0" | 1.5" | 1.5" |
| 1.5 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 1.0" | 2.0" | 2.0" | 2.0" | 2.0" | 1.5" |
| 2 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.0" | 1.0" | 1.0" | 1.0" | 1.0" | 2.5" | 2.0" | 2.0" | 2.0" | 1.5" |
| 4 | 1.0" | 0.5" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 2.5" | 2.5" | 2.0" | 2.0" |
| 6 | 1.0" | 1.0" | 0.5" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 3.0" | 2.5" | 2.5" | 2.0" |
| 8 | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.0" | 1.0" | 1.0" | 1.0" | 3.0" | 3.0" | 2.5" | 2.5" | 2.0" |
| 10 | 1.0" | 1.0" | 1.0" | 0.5" | 0.5" | 1.5" | 1.5" | 1.0" | 1.0" | 1.0" | 3.5" | 3.0" | 2.5" | 2.5" | 2.0" |
| 12 | 1.0" | 1.0" | 1.0" | 1.0" | 0.5" | 1.5" | 1.5" | 1.0" | 1.0" | 1.0" | 3.5" | 3.0" | 2.5" | 2.5" | 2.0" |

- EQUIPMENT INSULATION SCHEDULE:

1. As noted on the drawings or per ASHRAE 90.1 Schedule.

# END OF SECTION 220700

# SECTION 230700 - HVAC INSULATION

# PART 1 - GENERAL

1.1     RELATED DOCUMENTS

1.2     SUMMARY

1.3     SUBMITTALS FOR INFORMATION

1.4     QUALITY ASSURANCE

# PART 2 — PRODUCTS

2.1     INSULATION MATERIALS

2.2     FACTORY APPLIED JACKETS

2.3     FIELD APPLIED JACKETS

2.4     OUTDOOR DUCTWORK

# PART 3 — EXECUTION

3.1     EXAMINATION

3.2     GENERAL INSULATION REQUIREMENTS

3.3     PIPING INSULATION

3.4     PIPING INSULATION: PIPE & TANK INSULATION AND KWIKFLEX

3.5     EQUIPMENT INSULATION - GLASS MINERAL WOOL

3.6     INTERNAL DUCT LINING

3.7     FLEXIBLE GLASS MINERAL WOOL BLANKET

3.8     ROUND DUCTWORK - PIPE & TANK INSULATION AND KWIKFLEX

3.9     GLASS MINERAL WOOL DUCTWORK

3.10   INSULATION SCHEDULES

# SECTION 230700 - HVAC INSULATION

# PART 1 — GENERAL

# 1.1     RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specifications, apply to this Section.

# 1.2	SUMMARY

A.	Section Includes:

1.	Insulation Materials:

a.	Piping insulation, jacketing and accessories

b.	Equipment insulation and jacketing or coatings

c. 	Mastics and Tapes

e.	Laminated self-adhesive water and weather seal: such as VentureClad

f.	PVC Fittings and inserts

g.	Pre-formed; formaldehyde free glass mineral wool fittings

2.	References

a.	ASTM International (ASTM)

b.	American Society of Heating, Refrigerating, and Air Conditioning Engineers, Inc. (ASHRAE)

c.	North American Insulation Manufacturers Association (NAIMA)

d.	National Fire Protection Association (NFPA)

e.	Sheet Metal and Air Conditioning Contractors National Association, Inc. (SMACNA)

f.	Underwriter’s Laboratories (UL)

g.	Underwriter’s Laboratories Environment (UL Environment)

3.	Definitions

a.	Thermal conductivity (k value): BTU-in. / (hr ∙ ft² ∙ °F)

b.	UL GREENGUARD provides independent, third-party, Indoor Air Quality (IAQ) certification of products for emissions of respirable particles and Volatile Organic Compounds (VOC’s), including formaldehyde and other specific product-related pollutants. Certification is based upon criteria used by EPA, OSHA and WHO.

c.	IAQ: Indoor Air Quality

d.	EPA: Environmental Protection Agency

e.	WHO: World Health Organization

f.      ASJ+: All Service Jacket composed of aluminum foil reinforced with glass scrim bonded to a kraft paper interleaving with an outer film layer leaving no paper exposed.

g.	ASJ: All Service Jacket

h.	SSL+: Self-sealing Advanced Closure System

i.	SSL: Self-Sealing Lap

j.	FSK: Foil-Scrim-Kraft; jacketing

k.	PSK: Poly-Scrim-Kraft; jacketing

l.	PVC: Polyvinyl Chloride

m.	FRP: Fiberglass Reinforced Plastic

n.    Glass Mineral Wool:  Interchangeable with fiber glass, but replacing the term with the 
                                   intent to disassociate and differentiate Glass Mineral Wool from the potential health and 
                                   safety risk of special purpose or reinforcement products that do not meet the bio soluble 
                                   criteria of insulation made from glass.

o.     ECOSE® Technology: a revolutionary new binder system based on rapidly 			          	         renewable bio-based materials rather than petroleum-based chemicals commonly 			         used in other glass mineral wool insulation products. ECOSE® Technology reduces the 		         binder embodied energy by up to 70% and does not contain phenol, formaldehyde, 			         acrylics or artificial colors.

p.     UL GREENGUARD Gold Certification: (Formerly known as  
                                   GREENGUARD Children & Schools Certification) offers stricter certification 
                                   criteria, considers safety factors to account for sensitive individuals (such as children 
                                   and the elderly), and ensures that a product is acceptable for use in environments such 
                                   as schools and healthcare facilities. It is referenced by both The Collaborative for High 
                                   Performance Schools (CHPS) and the Leadership in Energy and Environmental Design 
                                   (LEED) Building Rating Systems.

q.      UL Environment Formaldehyde Free Verification Requirements: for a

product to be verified as formaldehyde free, product samples must have a measured

emission factor of less than or equal to 5 µg/m2 h at 24 elapsed hours or 3 µg/m2 h at

336 elapsed hours. An emission factor of 5 µg/m2 h, corresponds to a measured

chamber concentration of 2.5 µg/m3 for a typical building ratio of 0.5 m2/m3. This

chamber concentration is comparable to, or below typical outdoor air concentrations.

This demonstrates that the formaldehyde exposure from products labeled as

formaldehyde free will not contribute to airborne formaldehyde concentrations at

greater levels than those found in the natural outdoor environment.

r.       Declare and The Living Building Challenge – The Living Building Challenge is a

philosophy, advocacy tool and certification program that addresses development at

all scales. The purpose of The Living Building Challenge is to define the most

advanced measure of sustainability in the built environment today and acts to

diminish the gap between current limits and ideal solutions. Declare supports The

Living Building Challenge by providing a transparent materials database that project

teams can select from to meet Imperative 11.

s.      Imperative 11, Red List – requires that manufacturers disclose the ingredients in their

products to insure that they are free of Red List chemicals and materials. The Red

List represents the “worst in class” materials, chemicals and elements known to pose

serious risks to human health and the greater ecosystem.

t.      Underwriter’s Laboratories Environment (UL Environment): offers

independent green claims validation, product assessment and certification.

UL GREENGUARD provides third-party credibility for sustainable products.

u.      UL Environment Claims Validation (ECV): service and label tests a manufacturer’s

product and validates that the environmental claims they make in their marketing and

packaging materials are factual. This Environmental Claims Validation (ECV) service

will allow manufacturers to verify that their products contain a quantifiable amount of

recycled content and, as such, help limit raw material extraction and reduce landfill

waste. It also will enable products to qualify for LEED® points under

Pilot Credit 43: MR – Certified Products.

v       EUCEB: exonerated fiber from a health and safety standpoint by the European

Certification Board process.

w.     Recycled content – Post-Consumer: materials such as bottled glass collected at

curbside or other collection sites after consumer use and used in the manufacturing

process to create a new product rather than being placed in a landfill or incinerated.

x.      Recycled content – Pre-Consumer (aka post-industrial): materials used or created

from one manufacturing process which are collected as scrap and placed back into

another manufacturing process rather than being placed in a landfill or incinerated.

y.      Polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or

Deca-BDE fire retardants: have been linked to adverse health effects after exposure

in low concentrations.

z.      UL Classified: UL has tested and evaluated samples of the product with respect to

certain properties of the product. UL Classifies products to:

Applicable UL requirements

Standards for safety

Standards of other National and International organizations

aa.    EPD: Environmental Product Declaration. A third party verified document that reports

environmental data of products based on the Life Cycle Assessment (LCA) and other

relevant information, and in accordance with the International Standard ISO 14025

(Type III Environmental Declarations)

B.	Related Sections:

1.	Division 22 Section "Plumbing Insulation"

# 1.3     SUBMITTALS FOR INFORMATION

A.	Product data: To include product description, manufacturer's installation instructions, and appropriate specification compliance for each application. Thickness is determined by Engineer and provided in a thickness schedule. Locations are dictated by project design.

B.	Samples and mockups of systems shall be provided upon engineer’s request.

C.    EPD Submittals: As certified by UL Environment.

D.	LEED Submittals:

1.	Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including   
printed statement of VOC content and chemical components.

2.	Product Data for Credit MR 5 Regional Materials: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

3.	LEED v 4, Product Data for Credit EA 2: For products and materials significant to the energy performance of a structure, provide documentation that indicates that insulation levels are significant to increasing the level of energy performance beyond the prerequisite standard.

4.	LEED v 4, Product Data for Credit MR 2: For products and materials to comply with Building Product Disclosure & Optimization, provide data/evidence that substantiates Environmental Product Declaration and Multi Attribute Optimization requirements.

5.	LEED v 4: Product Data for Credit MR 3: For products and materials to comply with requirements for regional materials, provide documentation indicating location of product or material, manufacturing location and the point of extraction, harvest, or recovery for each raw material. Include distance to Project, contractor cost for each regional material, and percent by weight that is considered regional.

6.	LEED v 4, Product Data for Credit MR 4: For products having recycled content documentation; indicating percentages by weight of post-consumer and pre-consumer recycled content. Include statement indicating cost for each product having recycled content.

7.	LEED v 4, Product Data for Credit EQ 2:  For products and materials to comply with low emittance standards, provide documentation substantiating that insulation products comply with requisite low emittance standards.

8.	LEED v 4, Product Data for Credit EQ 5: For products and materials to meet the standard for both thermal comfort design and thermal comfort control, provide data to support that insulation products are significant to thermal comfort design and thermal comfort control.

9.	LEED v 4, Product Data for Credit EQ 9: For products and materials that contribute to the design and performance of workspaces that promote occupants well-being, productivity, and communication, provide data/documentation supporting acoustical benefits of Glass Mineral Wool insulation products.

10.	Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that product complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small Scale Environmental Chambers."

# 1.4     QUALITY ASSURANCE

A.	Surface Burning Characteristics: Insulation and related materials shall have surface burning characteristics determined by test performed on identical products per UL 723 or ASTM E 84 mounted and installed as per ASTM E 2231. All testing shall be performed by a testing and inspecting agency acceptable to authorities having jurisdiction. Insulation, jacket materials, adhesives, mastics, tapes and cement material containers shall be labeled with appropriate markings of applicable testing and inspecting agency.

1.	Insulation installed indoors:  Flame spread index of 25 or less, and smoke developed index of 50 or less.

2.	Insulation installed outdoors:  Flame spread index of 75 or less, and smoke developed index of 150 or less.

B.	Store tapes, adhesives, mastics, cements, and insulation materials in ambient conditions in accordance with the recommendations of the manufacturer.

C.	Follow manufacturer’s recommended handling practices.

D.    Supply glass mineral wool insulation products that are manufactured using a minimum of 50% “post-consumer” recycled material.

E.	Supply glass mineral wool insulation products that are manufactured using a bio-based binder rather than non-renewable petroleum-based chemicals and with a binder that does not contain phenol, formaldehyde, or acrylics; whenever possible.

F.	Supply glass mineral wool insulation products that have achieved UL GREENGUARD Gold Certification and are verified formaldehyde free by UL Environment; whenever possible.

G.    Supply glass mineral wool products that are Living Building Challenge – Declare, Red List free; whenever possible.

H.    Products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE fire retardants; whenever available.

I.	WET: Contractor shall take precaution to protect insulation. Any glass mineral wool insulation that becomes wet or torn should be replaced at no additional cost.

1.    Air handling insulation used in the air stream must be discarded if exposed to liquid

water.

2.    Pipe Insulation with factory applied ASJ+ facing having been installed per manufacturer’s

installation recommendation which may experience intermittent exposure to liquid water after

installation may be exempted from removal and replacement requirements.

# PART 2 — PRODUCTS

# 2.1     INSULATION MATERIALS

A.	Insulation products shall not contain asbestos, lead, mercury, mercury compounds, or formaldehyde. Products shall be certified by UL GREENGUARD GOLD or Indoor Advantage Gold.

B.	Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

C.    Insulation materials applied to carbon steel shall be Mass Load Corrosion Rate (MLCR) tested per of ASTM C 1617.

D.	Manufacturers: Knauf Insulation, Proto Corporation, ICA Hamfab, VentureClad, or pre-approved substitute.

E.	Glass Mineral Wool: Knauf Insulation Earthwool™ 1000( Pipe Insulation with ECOSE® Technology, UL/ULC Classified, EPD Certified by UL Environment, Living Building Challenge – Declare, Red List free for unjacketed Pipe, meeting ASTM C 547 Type IV Grade A, ASTM C 585, ASTM C411 and ASTM C 795; rigid, molded; k value: ASTM C 335, 0.23 at 75(F (0.033 at 24(C) mean temperature. Maximum Service Temperature: 1000(F (538(C). Vapor Retarder Jacket: ASJ+/SSL+ conforming to ASTM C 1136 Type I, II, III, IV, & VIII secured with self-sealing longitudinal laps and matching ASJ+ butt strips. Verified to be formaldehyde free by UL Environment.

F.	Glass Mineral Wool: Knauf Insulation Earthwool™ Redi-Klad® 1000° Pipe Insulation with ECOSE® Technology, Component FHC 25/50 per ASTM E 84, EPD Certified by UL Environment, Living Building Challenge – Declare, Red List free, meeting ASTM C 547, ASTM C 585, ASTM C411 and ASTM C 795; rigid, molded; k value: ASTM C 335, 0.23 at 75( F (0.033 at 24( C) mean temperature. Maximum Service Temperature: 1000( F (538( C). Redi-Klad Jacket: VentureClad 5-ply weather and abuse resistant with self-seal lap. Zero permeability per

ASTM E 96-05; puncture resistance 35.4 kg (189.3 N) per ASTM D 1000; tear strength 4.3 lb. (19.4 N) per ASTM D 624; thickness 14.5 mils (0.0145″); tensile strength 68.0 lb./inch width [306 N (31 kg)/25 mm].

G.	Glass Mineral Wool: Knauf Pipe & Tank Insulation with ECOSE® Technology; semi-rigid, limited combustible meeting requirements of ASTM C 1393;  NRC 1.36; ASTM C 795, ASTM C447 and MIL-I-24244C, k value: ASTM C 177, 0.25 at 75( F (0.036 at 24(C) mean temperature. Maximum Service Temperature: 850(F (454(C). Compressive Strength: not less than 120 PSF (5.75 kPa) @ 10% deformation per ASTM C 165. Vapor Retarder Jacket: ASJ conforming to ASTM C 1136 Type II, FHC 25/50 per ASTM E 84.

H.	Glass Mineral Wool: Knauf KwikFlex™; semi-rigid glass mineral wool blanket in roll form, UL/ULC Classified ASJ and FSK, FHC 25/50 per ASTM E 84 PSK only, meeting requirements of UL 723, ASTM E 84, ASTM C 1393, ASTM C447 and ASTM C 356, k value: ASTM C 518, 0.24 at 75( F (0.035 at 24(C) mean temperature. Maximum Service Temperature: 850(F (454(C); maximum surface temperature for faced product: 150(F (66( C); maximum thickness @ 850( F: 4 inches (102 mm). Compressive Strength: not less than 25 PSF (1.2 kPa) @ 10% deformation per ASTM C 165. Vapor Retarder Jacket:  ASJ, FSK or PSK conforming to ASTM E 96, Procedure  A.

I.	Fitting Insulation: Insulate using pre-formed PVC fitting covers with glass mineral wool inserts. Alternatively, preformed formaldehyde free glass mineral wool; minimum 50% post-consumer recycled glass content, mitered glass mineral wool pipe insulation, pre-formed perlite, mitered perlite or calcium silicate may be used for some applications depending on the service conditions. These fittings shall be further protected by field-applied fitting covers or metal fittings as necessary.

J.	Rigid Glass Mineral Wool Board: Knauf Insulation Board with ECOSE® Technology, UL/ULC Classified unfaced, ASJ, FSK; FHC 25/50 per ASTM E 84 PSK only; meeting ASTM C 612 Type IA and IB; rigid. Verified to be formaldehyde free by UL Environment. Maximum Service Temperature: 450( F (232( C).

- Concealed Areas: Density: Minimum 3 PCF (48 kg/m3). k value: ASTM C 177, 0.23 at

75( F (0.033 at 24( C) mean temperature. Vapor Retarder Jacket: ASJ conforming to

ASTM C 1136 Type I, or FSK or PSK conforming to ASTM C 1136 Type II.

- Exposed Areas: Density: Minimum 6 PCF (96 kg/m3). k value: ASTM C 177, 0.22 at

75( F (0.032 at 24( C) mean temperature. Vapor Retarder Jacket: ASJ conforming to

ASTM C 1136 Type I, or FSK or PSK conforming to ASTM C 1136 Type II in combination with protective jacket where necessary.

K.	Rigid Glass Mineral Wool Board: Knauf Elevated Temperature (ET) Board with ECOSE® Technology, UL/ULC Classified, meeting ASTM C 612 Type IA, IB, and II; rigid, noncombustible and ASTM C447. Maximum Service Temperature: 1000( F (538( C). Density: 2.8 PCF

(45 kg/m3), k value: ASTM C 177, 0.25 at 100( F (0.036 at 38( C) mean temperature. Verified to be formaldehyde free by UL Environment.

L.	Semi-Rigid Glass Mineral Wool Board: Knauf Elevated Temperature (ET) Panel with ECOSE® Technology, UL/ULC Classified, meeting ASTM C 612 Type II and III; semi-rigid, noncombustible and ASTM C447. Maximum Service Temperature: 1000( F (538( C). Density: 2.4 PCF

(38 kg/m3), k value: ASTM C 177, 0.25 at 100( F (0.036 at 38( C) mean temperature. Verified to be formaldehyde free by UL Environment.

M.	Flexible Glass Mineral Wool Blanket: Knauf Elevated Temperature (ET) Blanket with ECOSE® Technology, UL/ULC Classified; flexible, noncombustible meeting ASTM C447. Maximum Service Temperature: 1000( F (538( C). Density: 1.1 PCF (18 kg/m3), k value: ASTM C 177,

0.28 at 100( F (0.040 at 38( C) mean temperature. Verified to be formaldehyde free by

UL Environment.

N.	Flexible Glass Mineral Wool Blanket:  Knauf Friendly Feel® Duct Wrap with ECOSE® Technology, UL/ULC Classified FSK, FHC 25/50 per ASTM E84 PSK only; meeting ASTM C 553 Types I, II and III, and ASTM C 1290; UL GREENGUARD Certified; flexible, limited combustible, k value: ASTM C 177, 0.29 at 75( F (0.042 at 24(C) mean temperature. Maximum Service Temperature -  Faced: 250(F (121(C); unfaced: 350(F (177(C). Vapor Retarder Jacket: FSK or PSK conforming to ASTM C 1136 Type II. Installation: Maximum allowable compression is 25%. Securement: Secured in place using outward cinching staples in combination with appropriate pressure-sensitive aluminum foil or PSK tape, or in combination with glass fabric and vapor retarder mastic. Density: concealed areas: Minimum 0.75 PCF (12 kg/m3); exposed areas: Minimum 1.0 PCF (16 kg/m3). Verified to be formaldehyde free by UL Environment.

O.	Glass Mineral Wool Duct Liner: Knauf Sonic XP™ Duct Liner with ECOSE® Technology,

UL/ULC Classified, conforming to ASTM C 1071 Type I and NFPA 90A & 90B; UL GREENGUARD Certified, or Knauf Rigid Plenum Liner with ECOSE® Technology, UL/ULC Classified, complying with ASTM C 1071 Type II and NFPA 90A & 90B, UL GREENGUARD Certified. K value: ASTM C 177, 0.24 at 75(F (0.035 at 24(C) mean temperature. Noise Reduction Coefficient (NRC): ASTM C 423 Type A Mounting, 0.45 or higher for ½″ product, 0.70 or higher for 1″ product. Maximum Air Velocity: 6000 FPM (1829 mpm) for Type I product, 5000 FPM (1524 mpm) for Type II product.

P.	Glass Mineral Wool Ductwork: Knauf Eclipse™ Air Duct Board with ECOSE® Technology, UL Certified, conforming to UL 181 Class 1 and NFPA 90A & 90B, UL GREENGUARD Certified, k value: ASTM C 177, 0.23 at 75(F (0.033 at 24(C) mean temperature. Maximum Temperature: 250(F (121(C). Maximum Internal Static Pressure: +/- 2″ water gauge. Maximum Air Velocity: 5000 FPM (1524 mpm). Type shall be EI-475 with FSK facing.  In applications where additional rigidity is required, for large spans, where extra strength is needed, or where energy codes require R-6 or greater, type shall be EI-800.

# 2.2     FACTORY APPLIED JACKETS

A.	ASJ+/SSL+:  All service jacket with Advanced Closure System self-sealing lap. All Service Jacket composed of aluminum foil reinforced with glass scrim bonded to a kraft paper interleaving with an outer film layer leaving no paper exposed; conforming to ASTM C 1136 Type I, II, III, IV & VIII; vapor retarder; with a self-sealing adhesive.

B.	ASJ: All service jacket. White-kraft paper bonded to aluminum foil and reinforced with glass fibers; conforming to ASTM C 1136; vapor retarder.

C.	FSK: Foil scrim kraft. Aluminum foil, fiberglass reinforced scrim with kraft backing; conforming to ASTM C 1136 Type 1; vapor retarder.

D.	PSK: Poly scrim kraft. Metalized polypropylene, fiberglass reinforced scrim with kraft backing; conforming to ASTM C 1136 Type 1; vapor retarder.

E.	Redi-Klad Jacket: VentureClad 5-ply weather and abuse resistant with self-seal lap,

Living Building Challenge – Declare, Red List free. Zero permeability per ASTM E 96-05; puncture resistance 35.4 kg (189.3 N) per ASTM D 1000; tear strength 4.3 lb. (19.4 N) per

ASTM D 624; thickness 14.5 mils (0.0145″); tensile strength 68.0 lb./inch width

[306 N (31 kg)/25 mm].

F.     Fire Retardant: products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE; whenever available.

# 2.3     FIELD APPLIED JACKETS

A.	PVC: Proto Corporation 25/50 or Indoor/Outdoor, UV resistant fittings, jacketing and accessories, white or colored.  Fitting cover system consists of pre-molded, high-impact PVC materials with glass mineral wool inserts. Glass mineral wool insert has a thermal conductivity (k value) of 0.26 at 75( F (0.037 at 24(C) mean temperature. Closures: stainless steel tacks, matching PVC tape, or PVC adhesive per manufacturer’s recommendations.

B.	 Aluminum Jacket: Alloy 3003 or 3105, minimum thickness per ASTM C 1729, smooth, corrugated, or stucco embossed with factory-applied moisture barrier.  Overlap shall be

2 inch (50 mm) minimum. Jacket shall be banded in place with ½” x 0.20” aluminum strapping fastened with aluminum wing seals.

C.    Stainless Steel Jacket: T-304, minimum per ASTM C 1729, smooth, corrugated or stucco embossed with factory-applied moisture barrier. Overlap shall be 2 inch (50 mm) minimum. Jacket shall be banded in place with ⅜” x 0.20 aluminum strapping fastened with stainless steel wing seals.

D.	Laminated Self-Adhesive Water and Weather Seals: permanent acrylic self-adhesive system; weather resistant, high puncture and tear resistance; meeting or exceeding requirements of

UL 723; applied in strict accordance with manufacturers’ recommendations.

E.     Fire Retardant: products shall contain no polybrominated diphenyl ethers (PBDE) such as Penta-BDE, Octa-BDE or Deca-BDE; whenever available.

# 2.4     OUTDOOR DUCTWORK

A.	Aluminum Jacket: 0.016 inch (0.406 mm) thick in smooth, corrugated, or embossed finish with factory applied moisture barrier. Overlap shall be 2 inch (50 mm) minimum. PVC Jacket: Proto Corporation Indoor/Outdoor, UV resistant, white. Closure shall be solvent weld adhesive or per manufacturers’ recommendations.

B.	Laminated Self-Adhesive Water and Weather Seals: applied per manufacturers’ recommendations.

C.	Either ductwork or insulation shall be installed so as to shed water and not allow standing water.

2.5      MASTICS

A.    Vapor Retarder Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-900 ASJ or KI-905 ASJ+

2.  Water Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.04 perm (0.026 metric perm) at 
                       40 mil dry film thickness.

3.  Service Temperature Range: -20°F to 120°F (-29°C to 82.2°C).

4.  Color: White

B.  Weather Barrier Mastics:

1.  Knauf Insulation EXPERT Mastics: KI-700 ASJ or KI-705 ASJ+

2.  Water Vapor Permeance: ASTM F 1249, 1.8 perm (1.2 metric perm)

3.  Service Temperature: 0°F to 180°F constant (-17.8°C to 82.2°C); -20°F to 200°F intermittent
                       (-29°C to 93°C)

4.  Solids: 58% by weight; 50% by volume

5.  Color: White

2.6      TAPES

A.    ASJ Tapes:

1.  Knauf Insulation EXPERT Tapes: ASJ Tape or ASJ+ Tape

2.  Width: 3 inches (75 mm) or 4 inches (101.6 mm)

3.  Thickness (Total): 14.3 mil (0.36 mm) – ASJ; 13.3 mil (0.34 mm) – ASJ+

4.  Adhesion: >4.8 Lbf / in. (840 N / m)

B.    FSK Tape:

1.  Knauf Insulation EXPERT Tapes: FSK Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 13.3 mil (0.34 mm)

4.  Adhesion: 6.5 Lbf / in. (1138 N / m)

C.   Aluminum Foil Tape:

1.  Knauf Insulation EXPERT Tapes: 2 Mil Foil Tape

2.  Width: 3 inch (75 mm) or 4 inch (101.6 mm)

3.  Thickness (Total): 7.3 mil (0.19 mm)

4.  Adhesion: 4.0 Lbf / in. (700 N / m)

# PART 3 — EXECUTION

# 3.1	EXAMINATION

A.	Verify that all piping, ductwork, and equipment are tested and approved prior to insulation installation.

B.	Verify that all surfaces are clean, dry and without foreign material before applying insulation materials.

# 3.2     GENERAL INSULATION REQUIREMENTS

A.	All materials shall be installed by skilled labor regularly engaged in this type of work.  All materials shall be installed in strict accordance with manufacturer’s recommendations, building codes, and industry standards.

B.	Locate insulation and cover seams in the least visible location.  All surface finishes shall be extended in such a manner as to protect all raw edges, ends and surfaces of insulation.

C.	On cold surfaces where a vapor seal must be maintained, insulation shall be applied with a continuous, unbroken moisture and vapor retarder.  All hangers, supports, anchors, or other projections secured to cold surfaces shall be insulated and vapor sealed to prevent condensation.

D.	All pipe insulation shall be continuous through walls, ceiling or floor openings or sleeves except where firestop or firesafing materials are required.

E.	Install multiple layers of insulation with longitudinal and circumferential joints staggered.

# 3.3     PIPING INSULATION: 1000° PIPE INSULATION AND REDI-KLAD PIPE INSULATION

A.	Locate all longitudinal pipe insulation jacketing laps in the least visible location.

B.     Longitudinal jacketing lap joints for pipe insulation installed on piping systems with operating temperatures below ambient shall be vapor sealed with factory-applied pressure sensitive adhesive, vapor retarder self-sealing lap. For proper sealing, lap joints shall be sealed with reasonable pressure being applied with a plastic squeegee. All circumferential joints shall be vapor sealed with factory furnished matching, pressure sensitive butt strips installed with reasonable pressure being applied with a plastic squeegee. Additionally, raw ends of pipe insulation sections shall be coated with vapor retarder mastic at 12’ to 21’ intervals; at the Engineer’s discretion, on straight piping and on either side of all fittings, flanges or valves. Vapor retarder mastic shall completely coat the ends of the pipe insulation and extend onto the bore of the pipe insulation and onto the jacketing a minimum of 2”.

C.	On high temperature piping, above 500°F (260°C), insulation shall be applied using double layer with staggered joints. When double layering, the inner layer should not be jacketed. All joints and ends must be firmly butted and secured with appropriate securement material.

D.	Metal shields shall be installed between hangers or supports and the piping insulation. Rigid insulation inserts shall be installed as required between the pipe and the insulation shields. Inserts shall be of equal thickness to the adjacent insulation and shall be vapor sealed as required. Insulation inserts shall be no less than the following lengths:

1½″ to 2½″ IPS	10″ long

3″ to 6″ IPS	12″ long

8″ to 10″ IPS	16″ long

12″ and over IPS	22″ long

E.	For piping exposed in mechanical rooms or high traffic areas, insulation shall be protected from abuse by the use of appropriate thickness of PVC jacketing, metal jacketing or laminated self-adhesive water and weather seals.

F.	For piping exposed to the elements install Redi-Klad with 4″ butt strips and self sealing lap or a jacketing that shall be UV resistant PVC with a minimum thickness of 0.020 inches, or 0.016 inches (0.406) thick aluminum with factory applied moisture barrier or 0.010 inches (0.254mm) thick stainless steel with a factory applied moisture barrier. Fitting covers shall be of similar materials. The insulation and jacketing shall be held firmly in place with a friction type Z lock or a minimum 2″ overlap joint. For systems operating below ambient, all PVC joints shall be sealed completely along the longitudinal and circumferential seams and installed so as to shed water. When required, all PVC circumferential joints shall be sealed by use of preformed butt strips; minimum 2″ wide or a minimum 2″ overlap. Butt strips shall overlap the adjacent jacketing a minimum ½ inch and be completely weather sealed. PVC Jacketing shall be limited to a maximum 20 inch OD of the insulation when exposed to direct sunlight. For systems operating above ambient, circumferential joints should overlap a minimum of 2″ and not be sealed. Insulation thickness for piping covered by PVC Jacketing shall be such that the surface temperature of the PVC does not exceed 125(F (52(C).

G.    Insulate valves, balancing valves and other devices requiring access with removable covers. Covers shall have a minimum k-factor of .26 using glass mineral wool blanket. Flame spread and smoke developed shall be 25/50 per ASTM E-84. Covers shall be completely overlapping and completely cover the adjacent insulation with seams and butt ends secure.

H.	Cold Piping Installation / High Abuse Systems

1.	On systems operating below freezing or systems operating in high abuse areas install Redi-Klad with 4″ butt strips and self sealing lap; or the ASJ+ jacket shall be protected with a PVC vapor retarding outer jacket. In addition, exposed ends of the insulation shall be sealed with a vapor retarder mastic installed per the manufacturer’s recommendations. Vapor stops, vapor retarder mastic applied in the insulation butt joint from the vapor retarder jacket to the bore of the pipe; a minimum of 2”, shall be applied at 12’ to 21’ intervals; at the Engineer’s discretion, and at each fitting to isolate any water incursion or transmission.

2.	On systems operating below ambient and in conditions of Design RH of 90% and above, it is recommended that the same guidelines be followed as listed above for below freezing applications.

# 3.4     PIPING INSULATION: PIPE & TANK INSULATION AND KWIKFLEX

A.	Apply on clean, dry surfaces.

B.	Cut to appropriate length using manufacturers’ stretchout guide for the specific pipe size. Add an additional 2 inches (51 mm) to 4 inches (102 mm) for a staple flap.

C.	Install insulation around the pipe circumference in a matter that insures a firm fiber mesh at all joints. Fasten the longitudinal lap with outward clinch staples placed 3 inches (76 mm) on center. As an alternative, individual sections may be fastened in place using continuous and overlapping strands of ¾” wide glass fiber filament tape around the insulation jacketing O.D. Longitudinal and circumferential joints shall be sealed with 4” wide matching pressure sensitive tape squeegeed along the entire length.

D.	For piping exposed to the elements, jacketing shall be UV resistant PVC with a minimum thickness of 0.020 inches, or 0.016 inches (0.406) thick aluminum with factory applied moisture barrier or 0.010 inches (0.254mm) thick stainless steel with a factory applied moisture barrier or laminated self-adhesive water and weather seals. Fitting covers shall be of similar materials. The insulation and jacketing shall be held firmly in place with a friction type Z lock or a minimum 2″ overlap joint. For systems operating below ambient, all PVC joints shall be sealed completely along the longitudinal and circumferential seams and installed so as to shed water. When required, all PVC circumferential joints shall be sealed by use of preformed butt strips; minimum 2″ wide or a minimum 2″ overlap. Butt strips shall overlap the adjacent jacketing a minimum ½ inch and be completely weather sealed. PVC Jacketing shall be limited to a maximum 20 inch OD of the insulation when exposed to direct sunlight. For systems operating above ambient, circumferential joints should overlap a minimum of 2″ and not be sealed. Insulation thickness for piping covered by PVC Jacketing shall be such that the surface temperature of the PVC does not exceed 125(F (52(C).

E.    On below ambient straight piping, vapor retarder mastic shall be applied to raw glass fiber ends at 12’ to 21’ intervals; at the Engineer’s discretion, and on either side of fittings, flanges or valves before taping. Mastic shall extend a minimum of 2 inches onto the bore of the pipe and 2 inches onto the jacketing.

# 3.5     EQUIPMENT INSULATION - GLASS MINERAL WOOL

A.	Apply insulation to the equipment surface with joints firmly butted and as close as possible to the equipment surface. Insulation shall be secured as required with mechanical fasteners or banding material. Fasteners shall be located a maximum of 3″ from each edge and spaced no greater than 12″ on center.

B.	For below ambient systems, vapor retarder jacketing shall overlap a minimum of 2″ at all seams and be sealed with appropriate pressure-sensitive tape or mastic. All penetrations and facing damage shall be covered with a minimum 2″ overlap of tape or mastic.

C.	Equipment insulation exposed to the elements shall be finished with minimum 0.030 inch thick, outdoor, weather resistant PVC; laminated self-adhesive water and weather seal material; or metal. All longitudinal joints shall be positioned so as to shed water; with a minimum 3″ overlap, and completely weather sealed. Laminated systems shall be applied per manufacturer’s recommendations.

D.	For high temperature applications, insulation may either be mounted in direct contact with the hot surface, in H-bar configuration, or pre-fabricated panel systems mounted away from the operating surface. When installing H-Bar or panel systems which are mounted away from the operating surface, convection stops shall be installed at a maximum of 8 feet along the vertical surfaces. Insulation may be applied over welded pins or studs up to ½″ in diameter. Insulation shall be held in place using mesh reinforcement or steel bands. Insulation shall not be compressed beyond a maximum of 1/8 inch at any point. Pins and studs shall be spaced a maximum of 4″ from each edge and no greater than 16″ on center. For temperatures above 500(F (260°C) and design thicknesses over 3″, insulation shall be applied using double layer with staggered joints.  Finish shall be minimum 0.020 inch thick PVC jacketing, insulating cement with canvas, glass cloth with mastic, or metal as specified on the drawings.

E.     For Equipment insulation exposed in mechanical rooms or subject to mechanical abuse, finish with minimum 0.020 inch thick PVC Jacketing or metal or laminated self-adhesive water and weather seal material. All other insulation shall be finished as appropriate for the location and service or as specified on the drawings.

# 3.6     INTERNAL DUCT LINING

A.	Duct Lining shall be applied in strict accordance with the latest edition of SMACNA’s “HVAC Duct Construction Standard Metal & Flexible” and NAIMA’s “Fibrous Glass Duct Liner Standard”.

B.	Length of mechanical fasteners shall be selected in accordance with the manufacturer’s recommendation as listed on each product.  Mechanical fasteners shall be installed perpendicular to the duct surface, and in no instance shall the pin compress the liner more than 1/8″ relative to the nominal thickness of the insulation.

C.	All exposed edges of the duct liner shall be coated with the factory applied edge coating or an adhesive which conforms to ASTM C 916.

D.	When duct lining is applied with an adhesive, the adhesive shall be applied to the sheet metal with a 90% minimum coverage.  All exposed duct liner edges not coated by the manufacturer shall be coated with the same adhesive.  All rips and tears shall be repaired using this same adhesive.

E.	Transverse joints shall be firmly butted with no gaps and coated with adhesive.  Longitudinal corner joints shall be overlapped and compressed.

F.	When air velocities are 4000 to 6000 FPM, metal nosing shall be applied to all upstream transverse edges to additionally secure the insulation.

# 3.7     FLEXIBLE GLASS MINERAL WOOL BLANKET

A.	Install Duct Wrap using manufacturer’s stretch-out tables to obtain specified R-value using a maximum compression of 25%.

B.	Minimum Installed R-value shall be per ASHRAE 90.1; UCC Code; or other design criteria.

C.	Firmly butt all joints.

D.	The longitudinal seam of the vapor retarder must be overlapped a minimum of 2 inches.

A 2 inch tab is provided on Knauf Friendly Feel( Duct Wrap for the circumferential seam. Secure all seams and overlaps using outward clinch staples approximately 6” on center. It is neither necessary nor desirable to adhere duct wrap to the duct surfaces with adhesive.

E.	Where vapor retarder performance is required, all penetrations and damage to the facing shall be repaired using pressure-sensitive tape matching the facing, or mastic prior to system startup. Pressure-sensitive tapes shall be a minimum 3 inches wide and shall be applied with moving pressure using a squeegee or other appropriate sealing tool. Closure shall have a 25/50 Flame Spread/Smoke Developed Rating per UL 723.

F.	Duct Wrap shall be additionally secured to the bottom of rectangular ductwork over 24 inches wide using mechanical fasteners on 18 inch centers.  Care should be exercised to avoid over-compression of the insulation during installation. Unfaced Duct Wrap shall be overlapped a minimum of 2 inches and fastened using 4 inch to 6 inch nails or skewers spaced 4 inches apart, or secured with a wire/banding system.  Care should be exercised to avoid damage to the Duct Wrap.

# 3.8     ROUND DUCTWORK - PIPE & TANK INSULATION AND KWIKFLEX

A.	Apply on clean, dry surfaces.

B.	Cut to appropriate length using manufacturers’ stretch-out guide for the specific duct size. Add an additional 2 inches (51 mm) to 4 inches (102 mm) for a staple flap.

C.	Wrap around the duct to ensure proper fit. Staple the lap on 3 inch (76 mm) centers with outward clinching staples.

D.	Ends shall be firmly butted and secured with matching butt strip material at each joint.

E.	On below ambient ductwork, appropriate UL approved vapor retarder shall be applied to all longitudinal and circumferential joints before application of butt strip material.

# 3.9     GLASS MINERAL WOOL DUCTWORK

A.	Ductwork shall be fabricated and installed in strict accordance with the latest edition of NAIMA’s “Fibrous Glass Duct Construction Standard” and manufacturer’s recommendations.

B.	Closure system shall be UL 181 tested and listed: Pressure-Sensitive Aluminum Foil Tapes:

UL 181 Part I (marked UL 181 A-P). Heat Sealable Closures: UL 181 Part II

(marked UL 181 A-H).  Mastics: UL 181 Part III (marked UL 181 A-M) with 3 inch wide glass fabric.

C.	All longitudinal and transverse joints having a 1½″ staple flap shall be secured with outward-cinching staples on approximate 2 inch centers and sealed with approved closure system.

D.	Transverse shiplap joints not having staples flaps, or transverse butt joints shall be secured with 8 inch long cross tabs running perpendicular to the joint seam on 12 inch centers.  Cross tabs shall be made from an approved closure tape.  The seam of the joint shall then be sealed with an approved closure system.

E.	Duct sections shall be additionally reinforced per NAIMA’s and manufacturer’s recommendations when necessary.  Reinforcement is dependent on duct width and operating pressure.

F.	Ductwork shall be suspended and supported as required on straight runs, at all turns, and at transitions to maintain proper alignment.  Hangers and supports shall be in strict accordance with NAIMA’s and manufacturer’s recommendations.

# 3.10      INSULATION SCHEDULES

- ASHRAE 90.1 – 2010 Requirements, Pipe Insulation

  - The minimum insulation thickness based upon ASHRAE 90.1 do not necessarily

represent the Economic Thickness of Insulation or the thickness required for

proper condensation control. Rather, they serve as minimum recommendations for

commercial applications. For recommended Economic Thickness and System Design,

install according to NAIMA 3E Plus or as specified.

# Minimum Pipe Insulation Thickness

Insulation Conductivity                                     Nominal Pipe or Tube Size (in.)

# Fluid Design

Operating Temp.            Conductivity               Mean Rating          <1         1 to < 1½       1½ to < 4       4 to <8         ≥8

Range (° F.)              Btu·in./(hr·ft²·°F)               Temp. °F.

# Heating and Hot Water Systems- Steam, Steam Condensate, Hot Water Heating and Domestic Water Systemsa,b,c,d

>350			0.32 – 0.34	           250	       4.5            5.0              5.0              5.0          5.0

251 – 350		0.29 – 0.32                   200                3.0            4.0              4.5              4.5          4.5

201 – 250                  0.27 – 0.30                   150                2.5            2.5              3.0              3.0          3.0

141 – 200                  0.25 – 0.29                   125                1.5            1.5              2.0              2.0          2.0

105 – 140                  0.22 – 0.28                   100                1.0            1.0              1.5              1.5          1.5

# Cooling Systems (Chilled Water, Brine, and Refrigerant) a,b,f

40 – 60                  0.21 – 0.27                    100               0.5            0.5              1.0               1.0          1.0

<40                     0.20 – 0.26                    100               0.5            1.0              1.0               1.0          1.5

a For insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:

# T = r{(1 + t/r)K/k – 1} where T = minimum insulation thickness (in.), r = actual outside radius of pipe (in.), t = insulation

# thickness listed in this table for applicable fluid temperature and pipe size, K = conductivity of alternate material at mean

# rating temperature indicated for the applicable fluid temperature (Btu·in.[hr·ft²·°F]), and k = the upper value of the

# conductivity range listed in this table for the applicable fluid temperature.

b These thicknesses are based on energy efficiency considerations only. Additional insulation is sometimes required

relative to safety issues/surface temperature. Issues such as water vapor permeability or surface condensation

sometimes require vapor retarders or additional insulation.

c For piping smaller than 1½” and located in partitions within conditioned spaces, reduction of these thicknesses by 1”

shall be permitted (before the thickness adjustment required in footnote a) but not to thicknesses below 1”.

d For direct-buried heating and hot water system piping, reduction of these thicknesses by 1.5” shall be permitted (before

thickness adjustment required in footnote a) but not to thicknesses below 1”.

e The table is based on steel pipe. Non-metallic pipes schedule 80 thickness or less shall use the table

values. For other non-metallic pipes having thermal resistance greater than that of steel pipe, reduced

thicknesses are permitted if documentation is provided showing that the pipe with the proposed insulation

has no more heat transfer per foot than a steel pipe of the same size with the insulation thickness shown on

the table.

f  For direct-buried cooling system piping, insulation is not required.

B.	NECESSARY PIPE INSULATION THICKNESS TO PREVENT CONDENSATION:

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 80°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 0.5” | 0.5” | 1.5” | 1.5” | 1.5” | 1.0” | 1.0” |
| 1 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 0.5” | 0.5” | 1.5” | 1.5” | 1.5” | 1.5” | 1.0” |
| 1.5 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 2.0” | 2.0” | 1.5” | 1.5” | 1.5” |
| 2 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 2.0” | 2.0” | 1.5” | 1.5” | 1.5” |
| 4 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 2.0” | 2.0” | 2.0” | 1.5” | 1.5” |
| 6 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 0.5” | 2.5” | 2.5” | 2.0” | 2.0” | 1.5” |
| 8 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 0.5” | 2.5” | 2.5” | 2.0” | 2.0” | 1.5” |
| 10 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 0.5” | 2.5” | 2.5” | 2.0” | 2.0” | 1.5” |
| 12 | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 1.0” | 2.5” | 2.5” | 2.0” | 2.0” | 1.5” |

| Jacket: ASJ (ε = 0.9) Wind Speed = 0 mph Ambient Temperature = 90°F |
| --- |
|  | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature | Relative Humidity & Operating Temperature |
| Pipe | 70% RH | 80% RH | 90% RH |
| Size | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F | 35°F | 40°F | 45°F | 50°F | 55°F |
| 0.5 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 0.5” | 0.5” | 2.0” | 1.5” | 1.5” | 1.0” | 1.0” |
| 1 | 0.5” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 2.0” | 2.0” | 2.0” | 1.5” | 1.5” |
| 1.5 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 1.0” | 2.0” | 2.0” | 2.0” | 2.0” | 1.5” |
| 2 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.0” | 1.0” | 1.0” | 1.0” | 1.0” | 2.5” | 2.0” | 2.0” | 2.0” | 1.5” |
| 4 | 1.0” | 0.5” | 0.5” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 1.0” | 3.0” | 2.5” | 2.5” | 2.0” | 2.0” |
| 6 | 1.0” | 1.0” | 0.5” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 1.0” | 3.0” | 3.0” | 2.5” | 2.5” | 2.0” |
| 8 | 1.0” | 1.0” | 1.0” | 0.5” | 0.5” | 1.5” | 1.0” | 1.0” | 1.0” | 1.0” | 3.0” | 3.0” | 2.5” | 2.5” | 2.0” |
| 10 | 1.0” | 1.0” | 1.0” | 0.5” | 0.5” | 1.5” | 1.5” | 1.0” | 1.0” | 1.0” | 3.5” | 3.0” | 2.5” | 2.5” | 2.0” |
| 12 | 1.0” | 1.0” | 1.0” | 1.0” | 0.5” | 1.5” | 1.5” | 1.0” | 1.0” | 1.0” | 3.5” | 3.0” | 2.5” | 2.5” | 2.0” |

- ASHRAE 90.1 – 2010 REQUIREMENTS – DUCT INSULATION

# Minimum Duct Insulation R-Value a, Cooling and Heating Only Supply Ducts and Return Ducts

Duct Location

Climate			Ventilated      Unvented Attic	Unvented Attic	Unconditioned                Indirectly	 Buried

Zone            Exterior           Attic          Above Insulated           with Roof                Space b              Conditioned Space c

Ceiling                  Insulation a

# Heating – Only Ducts

1,2	            none             none                   none                          none                        none                            none                         none

3                      R – 3.5           none                   none                         none                        none	                 none                         none

4                      R – 3.5           none                   none                         none                        none                             none                         none

5                      R – 6.0         R – 3.5                 none                         none                        none                             none                       R – 3.5

6                      R – 6.0	  R – 6.0                R – 3.5                       none                        none                             none                       R – 3.5

7                      R – 8.0	  R – 6.0                R – 6.0                       none                      R – 3.5                           none                       R – 3.5

8                      R – 8.0         R – 8.0                R – 6.0                       none                      R – 6.0                           none                       R – 6.0

# Cooling – Only Ducts

1                      R – 6.0         R – 6.0                 R – 8.0                    R – 3.5                     R – 3.5                           none                      R – 3.5

2                      R – 6.0         R – 6.0                 R – 6.0                    R – 3.5                     R – 3.5                           none                      R – 3.5

3                      R – 6.0         R – 6.0                 R – 6.0                    R – 3.5                     R – 1.9                           none                        none

4                      R – 3.5         R – 3.5                 R – 6.0                    R – 1.9                     R – 1.9                           none                        none

5,6                    R – 3.5         R – 1.9                 R – 3.5                    R – 1.9                     R – 1.9                           none                        none

7,8                    R – 1.9         R – 1.9                 R – 1.9                    R – 1.9                     R – 1.9                           none                        none

# Return Ducts

1 to 8                R – 3.5         R – 3.5                 R – 3.5                     none                         none                              none                        none

a Insulation R – values, measured in (hr· ft²· °F)/Btu, are for the insulation as installed and do not include film resistance. The

required minimum thicknesses do not consider water vapor transmission and possible surface condensation. Where exterior

walls are used as plenum walls, wall insulation shall be required by the most restrictive condition of Section 6.4.4.2 or Section 5.

Insulation resistance measured on a horizontal plane in accordance with ASTM C518 at a Mean temperature of 75° F at the

installed thickness.

b Includes crawlspaces, both ventilated and non-ventilated.

c Includes return air plenum with or without exposed roofs above.

- (cont.)    ASHRAE 90.1 – 2010 REQUIREMENTS – DUCT INSULATION

# Minimum Duct Insulation R-Value a, Combined Heating and Cooling Supply Ducts and Return Ducts

Duct Location

Climate			Ventilated      Unvented Attic	Unvented Attic	Unconditioned                Indirectly	 Buried

Zone            Exterior           Attic          Above Insulated           with Roof                Space b              Conditioned Space c

Ceiling                  Insulation a

# Supply Ducts

1	          R – 6.0           R – 6.0              R – 8.0                     R – 3.5                   R – 3.5                         none                       R – 3.5

2                     R – 6.0           R – 6.0               R – 6.0	                   R – 3.5	       R – 3.5	              none                        R – 3.5

3                     R – 6.0           R – 6.0               R – 6.0	                   R – 3.5	       R – 3.5                         none	                 R – 3.5

4                     R – 6.0           R – 6.0               R – 6.0	                   R – 3.5	       R – 3.5	               none                       R – 3.5

5                     R – 6.0           R – 6.0               R – 6.0                     R – 1.9	       R – 3.5                         none                       R – 3.5

6                     R – 8.0	    R – 6.0              R – 6.0                     R – 1.9                   R – 3.5                         none                       R – 3.5

7                     R – 8.0	    R – 6.0              R – 6.0                     R – 1.9                   R – 3.5                         none                        R – 3.5

8                     R – 8.0           R – 8.0               R – 8.0                     R – 1.9                   R – 6.0                         none                       R – 6.0

# Return Ducts

1 to 8               R – 3.5           R – 3.5               R – 3.5                      none                        none                           none                        none

a Insulation R – values, measured in (hr· ft²· °F)/Btu, are for the insulation as installed and do not include film resistance. The

required minimum thicknesses do not consider water vapor transmission and possible surface condensation. Where exterior walls

are used as plenum walls, wall insulation shall be required by the most restrictive condition of Section 6.4.4.2 or Section 5.

Insulation resistance measured on a horizontal plane in accordance with ASTM C518 at a Mean temperature of 75° F at the

installed thickness.

b Includes crawlspaces, both ventilated and non-ventilated.

c Includes return air plenum with or without exposed roofs above.

D.	IECC CODE REQUIREMENTS

# Compliance With Uniform Construction Code

# TABLE 503.3.3.3

MINIMUM DUCT INSULATION

| ANNUAL HEATING DEGREE DAYS | Insulation R-value (hr·ft²·ºF.)/Btu |
| --- | --- |
|  | Ducts in unconditioned attics or outside building | Ducts in unconditioned basements, crawl spaces, garages, and other unconditioned spaces |
|  | Supply | Return | Supply | Return |
| Below 1,500 | 8 | 8 | 5 | 5 |
| 1,500 to 3,500 | 8 | 8 | 5 | 5 |
| 3,501 to 7,500 | 8 | 8 | 5 | 5 |
| Above 7,500 | 8 | 8 | 5 | 5 |

- All ductwork, air handlers and filter boxes must be sealed. Joints and seals shall comply with Section 603.9

of the International Mechanical Code.

# Exceptions:

1.    When located within equipment.

2.    When the design temperature difference between the interior and exterior of the duct or plenum does not exceed 15° F. (8° C).

# Systems to Achieve Required R-values For ASHRAE 90.1 and IECC

# R – 5:

- Air Duct Board – 1-1/2″ thick (R 6.5)

- Sheet metal ductwork with .75 PCF 2″ Duct Wrap (R 5.6 @ 25% compression)

- Sheet metal ductwork with 1.5 PCF 1-1/2″ thick rotary* Duct Liner (R 6.0)

# R – 8:

- Air Duct Board – 2″ thick  (R 8.7)

- Sheet metal ductwork with .75 PCF 3″ thick Duct Wrap  (R 8.4 @ 25% compression)

- Sheet metal ductwork with 1.5 PCF 2″ thick rotary* Duct Liner  (R 8.0)

* Textile Duct Liner may not achieve the required R-value.

E.	MINIMUM DUCT WRAP INSULATION (INSTALLED) TO PREVENT CONDENSATION

| Jacket: Aged Aluminum Foil or Galvanized Sheet Metal (ε = 0.2) Wind Speed = 0 mph |
| --- |
| Operating Temperature: 45°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 2.2 | 3.3 | 4.3 | 4.3 | 5.4 |
| 70% | 3.3 | 5.4 | 6.5 | 7.6 | ** |
| 80% | 7.0 | ** | ** | ** | ** |
| Operating Temperature: 55°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 1.1 | 2.2 | 3.3 | 3.3 | 4.3 |
| 70% | 1.1 | 3.3 | 4.3 | 6.5 | 6.5 |
| 80% | 3.3 | 6.5 | ** | ** | ** |
| Operating Temperature: 65°F |
|  | Ambient Temperature |
| Rel. Humidity | 70°F | 80°F | 90°F | 100°F | 110°F |
| 60% | 1.1 | 1.1 | 2.2 | 3.3 | 4.3 |
| 70% | 1.1 | 1.1 | 3.3 | 5.4 | 6.5 |
| 80% | 2.2 | 3.3 | 6.5 | ** | ** |
| 90% | 6.5 | ** | ** | ** | ** |

** Necessary R-value is greater than one typically supplied in duct wrap.  Please consult manufacturer.

F.	GLASS MINERAL WOOL DUCTWORK - REINFORCEMENT SCHEDULES

1.     Tie Rod System (Positive Pressure Only)

| Positive | Inside | TYPE 475 BOARD | TYPE 800 BOARD |
| --- | --- | --- | --- |
| Static Pressure | Duct Dimension (inches) | No. Rods Across Dimension | Maximum Longitudinal Spacing | No. Rods per 4 ft. Section | No. Rods Across Dimension | Maximum Longitudinal Spacing | No. Rods per 4 ft. Section |
|  | 0-36 |  | * |  |  | * |  |
|  | 37-42 | 2 | 24" | 4 | 2 | 48" | 2 |
| 0 thru ½" | 43-48 | 2 | 24" | 4 | 2 | 48" | 2 |
| W.G. | 49-60 | 3 | 24" | 6 | 3 | 48" | 3 |
|  | 61-64 | 3 | 24" | 6 | 3 | 24" | 6 |
|  | 65-80 | 4 | 24" | 8 | 4 | 24" | 8 |
|  | 81-96 | 5 | 24" | 10 | 5 | 24" | 10 |
|  | 0-24 |  | * |  |  | * |  |
|  | 25-30 | 1 | 24" | 2 | 1 | 48" | 1 |
| Over ½" | 31-32 | 1 | 24" | 2 | 1 | 24" | 2 |
| Thru 1" | 33-36 | 2 | 24" | 4 | 2 | 24" | 4 |
| W.G. | 37-48 | 2 | 24" | 4 | 2 | 24" | 4 |
|  | 49-64 | 3 | 24" | 6 | 3 | 24" | 6 |
|  | 65-80 | 4 | 24" | 8 | 4 | 24" | 8 |
|  | 81-96 | 5 | 24" | 10 | 5 | 24" | 10 |
|  | 0-15 |  | * |  |  | * |  |
|  | 16-18 | 1 | 24" | 2 |  | * |  |
|  | 19-24 | 1 | 24" | 2 | 1 | 24" | 2 |
| Over 1" | 25-32 | 1 | 16" | 3 | 1 | 24" | 2 |
| Thru 2" | 33-48 | 2 | 16" | 6 | 2 | 24" | 4 |
| W.G. | 49-60 | 3 | 16" | 9 | 3 | 24" | 6 |
|  | 61-64 | 3 | 16" | 9 | 3 | 16" | 9 |
|  | 65-80 | 4 | 16" | 12 | 4 | 16" | 12 |
|  | 81-96 | 5 | 16" | 15 | 5 | 16" | 15 |

*	Straight ducts of these dimensions do not require reinforcement.  However, some fittings of these dimensions may require reinforcement.

# NOTES:

- Tie rods and washers must be no more than 16″ on center across duct dimension.

- Ducts of 48″ width and over require use of anti-sag devices.

- For duct dimensions over 96″, maintain tie rode spacing on 16 inch center across the duct dimension following longitudinal spacing for the design pressure.

- If dimensions require, tie rods run in both horizontal and vertical directions.

2.	Channel System (Positive and Negative Pressure)

|  |  | Max. Inside | TYPE 475 BOARD | TYPE 800 BOARD |
| --- | --- | --- | --- | --- |
| Static Pressure |  | Duct Dimension (inches) | Maximum Longitudinal Spacing | Channel Gauge | H Dimension (see note) | Maximum Longitudinal Spacing | Channel Gauge | H Dimension (see note) |
| 0 thru ½″ | negative | 0-30 |  | * |  |  | * |  |
| W.G. |  | 31-36 | 24″ | 22 | 1″ | 48″ | 22 | 1″ |
|  | positive | 0-36 |  | * |  |  | * |  |
|  |  | 37-42 | 24″ | 22 | 1″ | 48″ | 22 | 1″ |
| 0 thru ½″ | positive | 43-48 | 24″ | 22 | 1″ | 48″ | 22 | 1″ |
| W.G. | or | 49-60 | 24″ | 22 | 1″ | 48″ | 22 | 1½″ |
|  | negative | 61-72 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
|  |  | 73-84 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
|  |  | 85-96 | 24″ | 22 | 1¼″ | 24″ | 22 | 1″ |
|  |  | 0-24 |  | * |  |  | * |  |
|  |  | 25-30 | 24″ | 22 | 1″ | 48″ | 22 | 1″ |
|  |  | 31-36 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
| Over ½″ | positive | 37-42 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
| Thru 1″ | or | 43-48 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
| W.G. | negative | 49-60 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
|  |  | 61-72 | 24″ | 18 | 1″ | 24″ | 18 | 1″ |
|  |  | 73-84 | 24″ | 18 | 1¼″ | 24″ | 18 | 1¼″ |
|  |  | 85-96 | 24″ | 18 | 1¼″ | 24″ | 18 | 1¼″ |
|  |  | 0-15 |  | * |  |  | * |  |
|  |  | 16-18 | 24″ | 22 | 1″ |  | * |  |
|  |  | 19-24 | 24″ | 22 | 1″ | 24″ | 22 | 1″ |
| Over 1″ | positive | 25-36 | 16″ | 22 | 1″ | 24″ | 22 | 1″ |
| Thru 2″ | or | 37-48 | 16″ | 22 | 1″ | 24″ | 22 | 1¼″ |
| W.G. | negative | 49-60 | 16″ | 22 | 1″ | 24″ | 22 | 1¼″ |
|  |  | 61-72 | 16″ | 18 | 1″ | 16″ | 18 | 1″ |
|  |  | 73-84 | 16″ | 18 | 1¼″ | 16″ | 18 | 1¼″ |
|  |  | 85-96 | 16″ | 18 | 1½″ | 16″ | 18 | 1½″ |

*	Straight ducts of these dimensions do not require reinforcement.  However, some fittings of these dimensions may require reinforcement.

NOTES:	1.	Ducts of 48″ width and over require use of anti-sag devices.

|  | H |  | GAUGE AS SPECIFIED |  |
| --- | --- | --- | --- | --- |
|  |  |  | 3″ |  |

G.	GLASS MINERAL WOOL DUCTWORK - MAXIMUM HANGER SPACING

|  | Duct Size, Inches | Maximum Hanger Spacing |  |
| --- | --- | --- | --- |
|  | 48″ wide or greater | 4 ft. |  |
|  | Less than 48″ wide and less than 12″ high | 6 ft. |  |
|  | Width between 24″ & 48″ and greater than 24″ high | 6 ft. |  |
|  | Less than 48″ wide and height between 12″ & 24″ | 8 ft. |  |
|  | Width 24″ or less and height greater than 12″ | 8 ft. |  |

# END OF SECTION 230700