OMG Roofing Products	June 2019

153 Bowles Road

Agawam, Massachusetts 01001

Toll Free	800-633-3800

Fax	413-821-0417

Website	www.omgroofing.com

E-mail	info@omgroofing.com

Guide Specification

Specifier Notes:  This guide specification is written in Construction Specifications Institute (CSI) 3-Part Format in accordance with The CSI Construction Specifications Practice Guide, MasterFormat, SectionFormat, and PageFormat.

This Section must be carefully reviewed and edited by the Architect to meet the requirements of the Project and local building code.  Coordinate this Section with Conditions of the Contract, Division 01, other specification sections, and the Drawings.  Delete all Specifier Notes after editing this Section.

Section numbers and titles are based on MasterFormat 2018 Edition.

23 05 29.13

ROOFTOP PIPE SUPPORTS

Specifier Notes:  This section covers OMG Roofing Products “PipeGuard” rooftop pipe supports for plumbing, HVAC, and electrical pipes and conduits from 1/2-inch to 6-inch (13-mm to 150-mm) diameter and from 1-1/2 inches to 10 inches (40 mm to 255 mm) above the roof.  Consult OMG Roofing Products for assistance in editing this section for the specific application.

Consult OMG Roofing Products for custom rooftop pipe supports to address nonstandard heights and widths.

GENERAL

SECTION INCLUDES

Rooftop pipe supports.

RELATED REQUIREMENTS

Specifier Notes:  Edit the following list of related sections as necessary.  Limit the list to sections with specific information that the reader might expect to find in this section, but is specified elsewhere.

Section 22 05 29 – Hangers and Supports for Plumbing Piping and Equipment.

Section 23 05 29 – Hangers and Supports for HVAC Piping and Equipment.

Section 26 05 29 – Hangers and Supports for Electrical Systems.

SUBMITTALS

Specifier Notes:  Edit submittal requirements as necessary.  Delete submittals not required.

Submittals:  Comply with Division 01.

Product Data:  Submit manufacturer’s product data, including installation instructions.

Shop Drawings:  Submit manufacturer’s shop drawings indicating dimensions, materials, hardware, and installation layout including sizes and spacing.

Samples:  Submit manufacturer’s samples of each size of rooftop pipe support specified.

Manufacturer’s Certification:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

Maintenance Instructions:  Submit manufacturer’s maintenance instructions, describing semi-annual visual inspection of rooftop pipe supports and realignment as necessary.

Warranty Documentation:  Submit manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer’s Qualifications:  Manufacturer regularly engaged, for past 5 years, in manufacture of rooftop pipe supports of similar type to that specified.

DELIVERY, STORAGE, AND HANDLING

Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

Storage and Handling Requirements:

Store and handle materials in accordance with manufacturer’s instructions.

Keep materials in manufacturer’s original, unopened containers and packaging until installation.

Store materials in clean, dry area indoors.

Protect materials during storage, handling, and installation to prevent damage.

PRODUCTS

MANUFACTURER

OMG Roofing Products, 153 Bowles Road, Agawam, Massachusetts 01001.  800-633-3800.  Fax 413-821-0417.  www.omgroofing.com.  info@omgroofing.com.

Specifier Notes:  Specify if substitutions will be permitted.

Substitutions:  [Not permitted]  [Comply with Division 01].

Single Source:  Provide materials from single manufacturer.

ROOFTOP PIPE SUPPORTS

Rooftop Pipe Supports:  “PipeGuard”.

Supports small rooftop pipes with engineered, prefabricated pipe supports.

Installs without roof penetrations or damage to membrane roofing.

Sits freely on roof.

Weather resistant.

UV stable.

Specifier Notes:  Specify required models of “PipeGuard” rooftop pipe supports.  Delete models not required.

Model:  Mini.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

Pipe Support Height:  1-1/2 inches (40 mm).

Drainage Slots:  Prevent pipes from sitting in standing water.

Supports Nominal Pipe Size:  1/2 inch to 1-1/2 inches (10 mm to 40 mm).

Maximum Load Capacity per Support:  225 lbs (102 kg).

Model:  Small.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

Pipe Support Height:  3-1/2 inches (90 mm).

Drainage Slots:  Prevent pipes from sitting in standing water.

Supports Nominal Pipe Size:  3/4 inch to 2 inches (20 mm to 50 mm).

Maximum Load Capacity per Support:  650 lbs (295 kg).

Model:  Tall Small.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

Pipe Support Height:  6 inches (150 mm).

Drainage Slots:  Prevent pipes from sitting in standing water.

Supports Nominal Pipe Size:  3/4 inch to 2 inches (20 mm to 50 mm).

Maximum Load Capacity per Support:  650 lbs (295 kg).

Model:  Large.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

Pipe Support Height:  3-1/2 inches (90 mm).

Drainage Slots:  Prevent pipes from sitting in standing water.

Supports Nominal Pipe Size:  2-1/2 inches to 5 inches (60 mm to 125 mm).

Maximum Load Capacity per Support:  940 lbs (427 kg).

Model:  Strut.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

Strut Channel:  Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps.

Pipe Support Height:  4 inches (100 mm).

Width at Top:  6 inches (150 mm).

Accommodates single or multiple pipes.

Supports Nominal Pipe Size:  Single pipe up to 5 inches (125 mm).

Maximum Load Capacity per Support:  800 lbs (363 kg).

Model:  Height Adjustable Strut.

Material:  Smooth, flexible, black, EPDM rubber.

Protects roof system from damage due to movement.

First Strut Channel:  Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps placed on top of base support.

Second Strut Channel:

Placed above first strut channel.

Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps.

Height:  Adjustable with 2 zinc-plated threaded rods and nuts.

Pipe Support Heights:  Adjustable from 4 inches (100 mm) (after removing second strut channel or setting it above pipes) to 10 inches (255 mm).

Width at Top:  10 inches (255 mm).

Accommodates single or multiple pipes.

Supports Nominal Pipe Size:  Single pipe up to 6 inches (150 mm).

Maximum Load Capacity per Support:  160 lbs (73 kg).

Model:  Safety Yellow Strut.

Material:  Smooth, rigid, yellow, 100 percent recycled, high-density polyethylene (RHDPE).

Protects roof system from damage due to movement.

Compatible with all roof covers including PVC membranes.

Strut Channel:  Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps.

Pipe Support Height:  3-1/2 inches (90 mm).

Width at Top:  10 inches (255 mm).

Accommodates single or multiple pipes.

Supports Nominal Pipe Size:  Single pipe up to 6 inches (150 mm).

Maximum Load Capacity per Support:  1,000 lbs (454 kg).

Model:  Yellow Height Adjustable Strut.

Material:  Smooth, rigid, yellow, 100 percent recycled, high-density polyethylene (RHDPE).

Protects roof system from damage due to movement.

Compatible with all roof covers including PVC membranes.

First Strut Channel:  Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps placed on top of base support.

Second Strut Channel:

Placed above first strut channel.

Low profile, 1-5/8-inch (40-mm), galvanized steel, accepts standard strut clamps.

Height:  Adjustable with 2 zinc-plated threaded rods and nuts.

Pipe Support Heights:  Adjustable from 3-1/2 inches (90 mm) (after removing second strut channel or setting it above pipes) to a maximum of 10 inches (255 mm).

Width at Top:  10 inches (255 mm).

Accommodates single or multiple pipes.

Supports Nominal Pipe Size:  Single pipe up to 6 inches (150 mm).

Maximum Load Capacity per Support:  180 lbs (82 kg).

Model:  Yellow Height Adjustable Roller.

        - Material:  Smooth, rigid, yellow, 100 percent recycled, high-density polyethylene (RHDPE).

Protects roof system from damage due to movement.

Compatible with all roof covers including PVC membranes.

Height:  Adjustable with 2 zinc-plated threaded rods and nuts.

Pipe Support Heights:  Adjustable from 5-1/2 inches (140 mm) to a maximum of 11 inches (279 mm).

Width at Top:  10 inches (255 mm).

Supports Nominal Pipe Size:  Single pipe up to 4 inches (100 mm).

Maximum Load Capacity per Support:  180 lbs (82 kg).

ACCESSORIES

Specifier Notes:  Edit the following paragraph for the specific application.  Delete if not required.

Riser:  [1-inch-high (25-mm high)]  [2-inch-high (50-mm high)] EPDM rubber slab in 4-inch by 8-inch (100-mm by 200-mm) shape.

Sets freely on membrane roofing.

Rooftop pipe supports adhered with bonding adhesive directly to riser.

EXECUTION

EXAMINATION

Examine rooftop and membrane roofing to receive rooftop pipe supports.

Notify Architect of conditions that would adversely affect installation or subsequent use.

Do not begin installation until unacceptable conditions are corrected.

PREPARATION

Clear membrane roofing of loose gravel and ballast to allow base of each rooftop pipe support to sit flat on roofing.

Specifier Notes:  Consult manufacturer of membrane roofing for requirements of separator sheet between each rooftop pipe support and membrane roofing.

Install separator sheet between each rooftop pipe support and membrane roofing.

INSTALLATION

Install rooftop pipe supports in accordance with manufacturer’s instructions at locations indicated on the Drawings.

Specifier Notes:  Edit the following spacing of rooftop pipe supports for the specific application.  Consult OMG Roofing Products for more information.

Spacing of Rooftop Pipe Supports:

Pipe Diameters 2 inches to 5 inches (50 mm to 125 mm):  Maximum 10 feet (3.0 m) apart.

Pipe Diameter 1-1/2 inches (40 mm):  Maximum 8 feet (2.4 m) apart.

Pipe Diameters less than 1-1/2 inches (40 mm):  Maximum 6 feet (1.8 m) apart.

Place 1 additional support at every union and source and along with 1 at side of junctions.

Specifier Notes:  Include the following paragraph when specifying “PipeGuard” Mini, Small, Tall Small, Large, Strut, or Height Adjustable Strut rooftop pipe supports.  Edit the following paragraph for the specific application.

Apply proper adhesion method, if required to adhere rooftop pipe supports to membrane roofing.

Built-Up Bituminous, Modified Bituminous, and TPO Membrane Roofing:  Use 1-component, elastomeric, gun-grade polyurethane sealant.

EPDM Membrane Roofing:  Use 3-inch or 6-inch (76-mm or 150-mm) wide EPDM roofing seam tape.

PVC Membrane Roofing:  Weld PVC slip sheet to membrane roofing and adhere rooftop pipe supports with 1-component, elastomeric, gun-grade polyurethane sealant.

Specifier Notes:  Include the following paragraph when specifying “PipeGuard” Safety Yellow Strut, Yellow Height Adjustable Strut, or Yellow Height Adjustable Roller rooftop pipe supports.  Edit the following paragraph for the specific application.

Apply proper adhesion method, if required to adhere rooftop pipe supports to membrane roofing.

Built-Up Bituminous, Modified Bituminous, PVC, and TPO Membrane Roofing:  Use 1-component, elastomeric, gun-grade polyurethane sealant.

EPDM Membrane Roofing:  Use 3-inch or 6-inch (76-mm or 150-mm) wide EPDM roofing seam tape.

PROTECTION

Protect installed rooftop pipe supports to ensure that, except for normal weathering, supports will be without damage or deterioration at time of Substantial Completion.

END OF SECTION