# TANK INSULATION

1.	GENERAL

  - This standard sets forth specifications and acceptable products for rigid, semi-rigid, and

flexible insulation for use on tanks.

1.2	This standard covers systems operating at temperatures ranging from 1200 (F (649 (C).

1.3	This standard will address wall thickness and multiple layer recommendations.

2.	APPLICATIONS

2.1	Tank Wall Insulation

A thermal calculation should be performed to determine the proper insulation thickness to ensure either personnel protection or process control. Where the insulation thickness exceeds 3”, a multiple layer system is recommended.

2.1.1	COMPOSITION:

Basalt wool and organic binder which is non-combustible and asbestos free.

2.1.2	NOMINAL DENSITY:

The nominal density to be between 3 and 12 pcf.

2.1.3	MAXIMUM THERMAL CONDUCTIVITY:

The thermal conductivity shall not exceed the following:

BTU in./h Ft2 (F (W/m K)		Mean Temperature

0.32 (0.046)		200 (F (93 (C)

0.42 (0.061)		300 (F (149 (C)

0.50 (0.072)		400 (F (204 (C)

0.63 (0.091)		500 (F (260 (C)

2.1.4	MAXIMUM NON-FIBROUS (SHOT) CONTENT:

The percentage content of non-fibrous material (shot) shall not exceed 20% by weight.

2.1.5	LINEAR SHRINKAGE

The linear shrinkage, when tested at 1200 (F (649 (C), shall be less than 1%.

2.1.6	STRESS CORROSION:

The material must not promote or contribute to the corrosion of austenitic stainless steel.

2.1.7	SURFACE BURNING CHARACTERISTICS:

Shall not exceed

Flame Spread		5		Smoke Developed	0

2.1.8	NOISE REDUCTION COEFFICIENT:

The NRC shall not be less than 0.95.

2.1.9	WATER VAPOR SORPTION:

The water vapor sorption shall be less than 1% by weight.

Approved Manufacture(s):		Owens Corning Insulation or equal

Single or multiple layer - 		High Temperature Industrial Board Insulation

High Temperature Flexible Batt Insulation

2.2	Tank Top Insulation

A thermal calculation should be performed to determine the proper insulation thickness to ensure either personnel protection or process control.  Where the insulation thickness exceeds 3”, a multiple layer system is recommended.

2.2.1	COMPOSITION:

Basalt wool and organic binder which is non-combustible and asbestos free.

2.2.2	NOMINAL DENSITY

The nominal density to be between 8 and 12 pcf.