PART 1	GENERAL

1.1	SUMMARY

A.	Section includes:  Provide a complete polyurethane waterproofing membrane system including all applicable sealants and elastomeric flashings needed to prevent water penetration at locations indicated.

B.	Related work:

- Documents affecting work of this Section include, but are not necessarily limited to, General Conditions, Supplementary Conditions, and Sections in Division 1 of these Specifications.

- Tile: Section

- Sealants: Section 7900

- Concrete: Section 3300

1.2	SUBMITTALS

A	Product data:

1.	Materials list of items proposed to be provided under this Section;

2.	Manufacturer's specifications and other data needed to prove compliance with the specified requirements;

3.	Shop Drawings or catalog illustrations in sufficient detail to show installation and interface of the work of this Section with the work of adjacent trades;

4.	Manufacturer's current recommended installation procedures which, when approved by the Architect, will become the basis for accepting or rejecting actual installation procedures used on the Work.

- Written documentation of applicator's qualifications, including reference projects of similar scope and complexity, with current phone contacts of architects and owners for verification.

- Provide test documentation or manufacturer’s certification that membrane and tin set mortar has been tested by Tile Council of America or other accetable sources. Test results shall meet or exceed current ANSI requirements.

- Provide certification product and applications meet Metro Dade Product Notice of Approval.

1.3	QUALITY ASSURANCE

A.	Use adequate numbers of skilled workmen thoroughly trained and experienced in the necessary crafts and completely familiar with the specified requirements and methods needed for proper performance of the work of this Section.

B.	Applicator qualifications:

1.	Applicator shall have at least three years experience in installing materials of types specified and shall have successfully completed at least three projects of similar scope and complexity.

2.	Applicator shall designate a single individual as project foreman who shall be on site at all times during installation.

C.	Convene a pre-installation job-site conference four weeks prior to commencing work of this Section:

1.	Secure attendance by Architect, Contractor, applicator, and authorized representatives of the membrane system manufacturer and interfacing trades.

2.	Examine Drawings and Specifications affecting work of this Section, verify all conditions, review installation procedures, and coordinate scheduling with interfacing portions of the Work.

1.4	DELIVERY, STORAGE AND HANDLING

A.	Deliver materials to job site in manufacturer's unopened containers with all labels intact and legible at time of use.

B.	Maintain the products in accord with manufacturer's recommendations with proper precautions to ensure fitness of material when installed.

C.	Comply with pertinent provisions of Section 01620.

1.5	SUBSTRATE CONDITIONS

A.	General:

1.	Provide applicator with surfaces that are broom clean, dry, sound and free of voids, bugholes, rockpockets, honeycombs, protrusions, excessive roughness, foreign matter, frost, ice and other contaminants which may inhibit application or performance of the waterproofing membrane system.

2.	Using suitable abrasive methods, remove residue of form release, curing compound, chemical retarders and other surface treatments, laitance, mortar smear, sawcutting residue, mill scale, rust, loose material and other contaminants from concrete, masonry and ferrous metal surfaces to receive the work of this Section.

B.	Concrete:  Where work of this Section will be applied to concrete, provide applicator with surfaces that are smooth with finish equal to one that is light steel troweled followed by a fine hair broom. No curing compounds or sealers shall be used or must be removed prior to appllication of membrane.

D.	Decks:

1.	Slope deck surfaces to drains that have flanges at membrane level which are flush with deck surfaces.

2.	Rigidly install pipe, vents and other surface protrusions, properly flash them, and cover to prevent entry of membrane materials.

E.	Metal flashings:  Where metal flashings are substrate to waterproofing membrane, set the flashings in continuous bedding bead of urethane sealant; install sealant S-bead between metal laps and mechanically fasten to substrate along leading edges at every 4" on center, staggered linearly, to lay flat without fishmouths.

F.	Joints:  Configuration shall be consistent with this Section and with all other requirements of the Contract Documents.

1.6	WARRANTY

A.	Deliver to the Architect signed copies of the following written warranties against defective materials and workmanship for a period of five years following date of completion.  Warrant that installed waterproofing membrane system shall be free of defects including adhesive failure, cohesive failure, and waterproofing failure resulting from substrate cracking up to 1/16 inch.

1.	Manufacturer's standard warranty covering materials;

2.	Applicator's standard warranty covering workmanship.

PART 2	PRODUCTS

2.1	GENERAL

- Provide a complete "Tremco/Vulkem 350 or 360NF" fluid applied elastomeric waterproofing membrane system manufactured by Tremco Incorporated (800) 852-8173 . Provide membraen complying with ASTM C836-89a. Insure compatibiliuty of membrane installation with tile or stone setting bed. Provide membrane that is 79-100 percent solids pure polyurethane designed for waterproofing concealed building components subject to hydrostatic head;Designed for use under ceramic tile on thin set mortar bed;

2.2	ACCESSORIES

A.	Primer:  As recommended by waterproofing membrane system manufacturer;

B.	Joint backing:  Closed-cell, polyethylene rod as recommended by membrane manufacturer;

- Elastomeric sheet flashing: Tremco Dual Flex ( Flashing System or Sika "Combiflex" System.

D. Sealant:  1) non-moving joints use Vulkem 116/227), 2) expansion joint use sheet flashing system and  Vulkem 45SSL 3) moving joints use ( non-expansion) use Vulkem 45SSL , Tile joints use Spectrem 3, Spectrtem 4, Vulkem 45SSL or Dymeric 240FC.

E.	Protection board: none unless required: as approved by membrane manufacturer.

2.3	OTHER MATERIALS

A.	Provide other materials, not specifically described but required for a complete and proper installation, as selected by the Contractor and approved by the membrane system manufacturer as compatible, subject to the approval of the Architect.

PART 3	EXECUTION

3.1	SURFACE CONDITIONS

A.	Coordinate as required with other trades to assure proper and adequate provision in the work of those trades for interface with the work of this Section.

B.	Applicator shall examine the areas and conditions under which work of this Section will be performed.

1.	Verify conformance with manufacturer's requirements;

2.	Report unsatisfactory conditions in writing to the Architect;

3.	Do not proceed until unsatisfactory conditions are corrected.

3.2	PREPARATION

A.	Surface preparation and detailing procedures to be in accord with waterproof membrane system manufacturer's instructions and recommendations except where more stringent requirements are indicated.

B.	Clean all deck surfaces to receive membrane system in accord with manufacturer's instructions;  vacuum clean or blow clean with oil-free compressed air all surfaces to receive sealants, detailing materials or membranes immediately prior to installation. Exisitng membrane shall be compatible with the Vulkem system. Clean all existing membraen to be left in place of all containmiantes. Remove all loose or non-recommended membrane by means deemed neccessary.

C.	Rout, clean, prepare and detail surface cracks in accord with manufacturer's instructions;  install backer rod where required.

D.	Clean metal surfaces to bright metal by wire brushing or mechanical etching;  scuff-sand lead flashing and plastic surfaces.

E.	Prime surfaces in accord with manufacturer's instructions.

F.	Install 1/4" diameter backer rod into corner of all horizontal-to-vertical junctures subject to movement and cover with 1" detail cant of approved sealant;  install 1" detail cants at projections, curbs and other horizontal-to-vertical junctures.

G.	Install detail coats, joint and crack treatments, and liquid flashings in accord with manufacturer's instructions.

H.	Allow detail applications to cure in accord with manufacturer's instructions prior to general application of membrane.

3.3	APPLICATION

A.	General:  Install waterproofing system in accord with manufacturer's recommendations and instructions as applies to the Work except where more stringent requirements are indicated.

1.	Waterproofing membrane shall average 60 mil dry-film thickness (note: if over occupied space below use 90 mils).

2.	Apply base coat of membrane and allow to cure per manufactrue’s recommendations. After cure install a second coat of base membrane while wet broadcast to rejection, pre-bagged 20-30 mesh silica aggregate approved by the manufacturer of the membrane system into the wet membrane. Allow to cure (Vulkem 350 must cure for 72 hours, Vulkem 360NF must cure for 24 hours) prioir to tile installation.

B.	Verify proper dry condition of substrate using method recommended by membrane system manufacturer;  perform adhesion checks prior to general application of membrane system using field adhesion test method recommended by manufacturer.

C.	Mask off adjoining surfaces not to receive membrane system.

D.	Wipe clean all detail coats with white rags wetted with Xylene solvent;  do not saturate detail coat.

E.	Apply membrane uniformly and allow to cure in accord with manufacturer's instructions.

F.	Feather terminating edge when entire area cannot be completed in one day;  clean area 6" wide along terminating edge of membrane with Xylene solvent on clean white rags prior to startup on next working day;  use interlaminary primer per manufacturer's instructions as needed;  overlap existing work by 6" with new work.

G.	Flood test:  Plug drains on deck surfaces and use sand bags or other means to restrict runoff.  Flood deck with water to depth of 2" (50 mm) and allow to stand at least 24 hours;  repair leaks if occurs and retest.

- Install protection board or drainage mat  over cured membrane in accord with manufacturer's instructions if required.

- Install edge course of pavers as required using an epoxy modified or approved thin-set mortar.

# APPLICATION OF CEMENTITIOUS MATERIAL

1. Thin Set Applications

- Apply thin set adhesive and tile per the manufacturer’s recommendations insuring all materials                      and methods are in accordance with the guidelines accepted by the TILE COUNCIL OF AMERICA’S latest publications

- Thin set adhesive shall meet ANSI A 118.4 or ANSI A118.5 r as approved by Tremco.

  - Use approved Euclid Chemical Company cementitious material.

  - Grout shal conform to ANSI A108.10.

- All perimeter tile interfaces and control joints 10 feet on center shall have ¼ inch minimun joint formed by holding the tile away from the interface. Interface joint is to be sealed with THC 901,Vulkem 45SSL or Dymonic FC.

2. Thick Set Applications

- Install mortar bed and reinforcing (mandatory) following guidelines as noted by ANSI 108.1A directly over the last coat of the waterproofing membrane. Slope to drain @1/4 inch per foot.

- Provide uncloged weep holes at roof drains ( by others)

- Movement Joints installed per Method EJ 171 of the TCA guidelines.

- Grout shall conform to ANSI A108.10

3.5	PROTECTION AND CLEAN-UP

A.	Promptly remove primer or membrane system material from adjacent surfaces with MEK, Toluene or Xylene;  leave work area in broom clean condition.

B.	Prohibit traffic over completed work and protect against  work overhead until protection course is installed;  protect from damage until protected beneath overlaying work.