SECTION 09 29 00

USG SECUROCK® BRAND ULTRALIGHT GLASS-MAT SHEATHING

PART 2  GYPSUM PANEL PRODUCTS

MOISTURE- AND MOLD-RESISTANT REGULAR AND TYPE X GLASS-MAT GYPSUM 	SHEATHING

ASTM C1177, Standard Specification for Glass Mat Gypsum Substrate for Use as Sheathing, for 1/2 in. (12.7 mm) Regular, 5/8 in. (15.9 mm) Type X and glass mat water-resistant gypsum substrate

Basis of Design: Subject to compliance with project requirements, the design is based on the following: United States Gypsum Company, USG Securock® Brand UltraLight Glass-Mat Sheathing

UL Type Designation: [1/2 in. (12.7 mm): Not applicable] [5/8 in. (15.9 mm): “USGX”]

ASTM E136 Noncombustibility: Meets

ASTM E84 Surface-Burning Characteristics

Flame Spread: [1/2 in. (12.7 mm): 0] [5/8 in. (15.9 mm): 0]

Smoke Developed: [1/2 in. (12.7 mm): 0] [5/8 in. (15.9 mm): 0]

Class A (Flame spread not greater than 25 and smoke developed not greater than 450): Meets

ASTM C473, Standard Test Methods for Physical Testing of Gypsum Panel Products

Core Hardness

Field: {1/2 in. [12.7 mm] (Not less than 15 lbf (67 N)): Meets} {5/8 in. [15.9 mm] (Not less than 15 lbf (67 N)): Meets}

End: {1/2 in. [12.7 mm] (Not less than 15 lbf (67 N)): Meets} {5/8 in. [15.9 mm] (Not less than 15 lbf (67 N)): Meets}

Edge: {1/2 in. [12.7 mm] (Not less than 15 lbf (67 N)): Meets} {5/8 in. [15.9 mm] (Not less than 15 lbf (67 N)): Meets}

Flexural Strength

Parallel: {1/2 in. [12.7 mm] (Not less than 80 lbf (356 N)): Meets} {5/8 in. [15.9 mm] (Not less than 100 lbf (445 N)): Meets}

Perpendicular: {1/2 in. [12.7 mm] (Not less than 100 lbf (445 N)): Meets} {5/8 in. [15.9 mm] (Not less than 140 lbf (623 N)): Meets}

Nail Pull Resistance: {1/2 in. [12.7 mm] (Not less than 80 lbf (356 N)): Meets} {5/8 in. [15.9 mm] (Not less than 90 lbf (400 N)): Meets}

Humidified Deflection: {1/2 in. [12.7 mm] (Not greater than 1/4 in. (6 mm)): Meets} {5/8 in. [15.9 mm] (Not greater than 1/8 in. (3 mm)): Meets}

Average Water Absorption (Not greater than 10% by weight after two-hour immersion): Meets

ASTM D3273, Standard Test Method for Resistance to Growth of Mold on the Surface of Interior Coatings in an Environmental Chamber: [1/2 in. (12.7 mm): 10] [5/8 in. (15.9 mm): 10]

Thickness: [1/2 in. (12.7 mm)] [5/8 in. (15.9 mm)]

Length: 8-12 ft. (2438-3658 mm)

Width: 48 in. (1219 mm)

Weight: [1/2 in. (12.7 mm): 1.7 lb./sq. ft. (8.3 kg/sq. m.)] [5/8 in. (15.9 mm): 2.2 lb./sq. ft. (10.7 kg/sq. m.)]

Edge: Square

Disclaimer:  The USG Product Specifications contained herein are intended for use as product reference material by architects, engineers, other design professionals, contractors, building code officials, or other competent construction industry trade professionals having an interest in the selection, specification and use of products manufactured by the subsidiaries of USG Corporation. The specifications are intended solely as technical support incident to the sale and use of USG products and not intended to be a substitute for the design review and approval of the licensed design professionals for the project.  These materials may be printed and/or transferred electronically solely as needed by the user. Because electronic files can be modified by other parties, without notice or indication of such modifications, modification of USG Product Guide Specifications is the sole responsibility of the Design Professional.