SECTION 09 29 00

USG SHEETROCK® BRAND ECOSMART PANELS FIRECODE 30®

PART 2  GYPSUM PANEL PRODUCTS

SUSTAINABLE NON-TYPE X GYPSUM PANEL

ASTM C1396, Standard Specification for Gypsum Board, for 5/8 in. (15.9 mm) and non-Type X gypsum wallboard

Basis of Design: Subject to compliance with project requirements, the design is based on the following: United States Gypsum Company, USG Sheetrock® Brand EcoSmart Panels Firecode 30®

ISO 14040 Environmental Management, Life Cycle Assessment, Principles and Framework:

Carbon emissions per Gypsum Association; Industry Standard Type III EPD for North American Type X wallboard have a Global Warming Potential value of 277 CO2 eq.: 207 kg CO2/1000 sq. ft.

Primary energy from non-renewable resources per Gypsum Association; Industry Standard Type III EPD for North American Type X wallboard have a value of 4,100 MJ/1000 sq. ft.: 3,730 MJ/1000 sq. ft.

UL Type Designation: “FC30”

ASTM E136 Noncombustibility: Meets

ASTM E84 Surface-Burning Characteristics

Flame Spread: 15

Smoke Developed: 0

Class A (Flame spread not greater than 25 and smoke developed not greater than 450): Meets

ASTM C473, Standard Test Methods for Physical Testing of Gypsum Panel Products

Core Hardness

Field [Not less than 11 lbf (49 N)]: Meets

End [Not less than 11 lbf (49 N)]: Meets

Edge [Not less than 11 lbf (49 N)]: Meets

Flexural Strength

Parallel [Not less than 46 lbf (205 N)]: Meets

Perpendicular [Not less than 147 lbf (654 N)]: Meets

Nail Pull Resistance [Not less than 87 lbf (387 N)]: Meets

Humidified Deflection [Not greater than 5/8 in. (15.9 mm)]: Meets

Thickness: 5/8 in. (15.9 mm)

Length: 8-16 ft. (2438-4877 mm)

Width: 4 ft. (1219 mm)

Weight: 1.7 lb./sq. ft. (8.3 kg/sq. m.)

Edge: Tapered

Shear Value for Wood-Frame; Screws, 8 in. (203 mm) OC perimeter, 12 in. (305 mm) OC field: 75 plf

Shear Value for Wood-Frame; Nails, 4 in. (102 mm) OC perimeter, 7 in. (178 mm) OC field: 127 plf

Disclaimer:  The USG Product Specifications contained herein are intended for use as product reference material by architects, engineers, other design professionals, contractors, building code officials, or other competent construction industry trade professionals having an interest in the selection, specification and use of products manufactured by the subsidiaries of USG Corporation. The specifications are intended solely as technical support incident to the sale and use of USG products and not intended to be a substitute for the design review and approval of the licensed design professionals for the project.  These materials may be printed and/or transferred electronically solely as needed by the user. Because electronic files can be modified by other parties, without notice or indication of such modifications, modification of USG Product Guide Specifications is the sole responsibility of the Design Professional.