# SECTION 036000

# GROUTING

PART 1 GENERAL

  - SUMMARY

- This section specifies pumping applications of cementitous, non-shrink, non-metallic grout under steel column base plates, steel joists and beam bearing plates and elsewhere as indicated.

  - RELATED SECTIONS

- Section 033000 – Cast in Place Concrete

- Section 034000 – Precast Concrete

  - REFERENCES

- American Society for Testing and Materials

  - ASTM C-78 – Test Method for Flexural Strength of Concrete.

  - ASTM C-109 – Test Method for Compressive Strength of Hydraulic Cement Mortars (Using 2 in. or 50 mm. Cube Specimens).

  - ASTM C-266 – Test Method for Time of Setting of Hydraulic-Cement Paste by Gillmore Needles.

  - ASTM C-882 – Test Method for Bond Strength of Epoxy-Resin Systems Used With Concrete by Slant Shear.

  - ASTM C-939 – Test method for Flow of Grout for Pre-placed Aggregate Concrete (Flow Cone Method).

  - ASTM C-1090 – Test Method for Measuring Change in Height of Cylindrical Specifications for Hydraulic-Cement Grout.

  - ASTM C-1107 – Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

- US Army Corps of Engineers CRD-C 621 – Specification for Non-Shrink Grout.

1.4	SUBMITTALS

- Submit under provisions of Section 013300 – Submittal Procedures

  - Product Data:  Manufacturer’s literature to include surface preparation, application instructions, recommendations and storage and handling requirements.

  - Test Data:  Confirm compliance and performance with specified requirements.

1.5	QUALITY ASSURANCE

- Applicator Qualifications:  Applicator must have prior experience applying specified product or similar products, or have manufacturer’s representative on site ensuring that preparation and application are performed correctly.

- Mockup:

  - Architect will select area for mockup.

2.	Prior notice will be given to architect four days before mockups will be applied.

3.	Architect must approve mockup before final product is applied.

4.	At the architect’s discretion, approved mockups may become incorporated into the final work.

  - DELIVERY, STORAGE & HANDLING

- Materials must be delivered in original, unopened containers with the manufacturer’s labels including product name and batch numbers.

- Store material in a dry area, above ground.  Protect cement from moisture and humidity.

  - ENVIRONMENTAL REQUIREMENTS

- Environmental Conditions:  Do not apply material when temperature is below 45°F (7oC) or when temperature is expected to fall below 45°F within 48 hours.

- Protection:  Precautions should be taken to avoid damage to any surface near the work zone.

PART 2 PRODUCTS

  - MANUFACTURER

- Acceptable Manufacturer:  US MIX Co., 112 South Santa Fe Drive, Denver, CO 80223, 800-397-9903, http://www.usspec.com.

  - MATERIALS

  - Non-Shrink Grout:

  - US SPEC MP Grout

  - Description:  Cement based, non-shrink, non-corrosive, non-metallic, pumpable and pourable grout.

  - Compliance:  ASTM C-1107, Grade B and CRD C-621.

  - Concrete Cleaner:

    - US SPEC Maxi Concrete Cleaner

    - Description:  Citrus-based concrete cleaner to clean and strip dirt, grease and laitance from surfaces to receive grout.

- Membrane Forming Curing Compound:

  - US SPEC Maxcure Resin Clear

  - Description:  Dissipating hydrocarbon resin curing compound.

  - Compliance:  ASTM C-309 Type I, Class B.

  - MATERIAL PROPERTIES

- ASTM C-78 – Flexural Strength (tested at fluid water ratio):

  - 3 Days – 700 psi (4.8 MPa) minimum

  - 28 Days – 1,100 psi (7.6 MPa) minimum

- ASTM C-109 – Compressive Strength (tested at fluid water ratio):

  - 1 Day – 2,000 psi (13.8 MPa) minimum

  - 3 Days – 3,500 psi (24.1 MPa) minimum

  - 7 Days – 5,500 psi (37.9 MPa) minimum

  - 28 Days – 7,000 psi (48.3 MPa) minimum

- ASTM C-266 – Rate of Set (tested at fluid water ratio):

  - Initial Set – 1 hour minimum

  - Final Set – 3.5 hours minimum, 4.5 hours maximum

- ASTM C-882 – Bond Strength (tested at fluid water ratio):

  - 7 Days – 1,750 psi (12.1 MPa) minimum

- ASTM C-1090 – Height Change (tested at fluid water ratio):

  - 1 Day – +0.007% minimum, +0.3% maximum

  - 28 Days – +0.016% minimum, +0.3% maximum

PART 3 EXECUTION

  - EXAMINATION

A.	Examine areas to receive grout.  Notify Engineer if surfaces are unacceptable.  Do not begin surface preparation or application until unacceptable conditions are corrected.

  - SURFACE PREPARATION

- Remove all grease, oil, dirt, laitance and unsound concrete.  Saturate area to receive grout with water.  Remove any puddles of water before placing grout.  Maintain a temperature between 45F and 90F (7oC and 32oC) prior to application and during initial 24 hours.

3.3	APPLICATION

- Mix and place grout according to manufacturer’s instructions.

- Prior to grouting, thoroughly saturate concrete surfaces for 24 hours; remove excess water.

- Grout may be rodded or tamped; do not vibrate.

3.4	FINISHING

- Ensure that grout “head” is at a 45 angle from bottom of plate to top of substrate.

3.5	CURING

- Place wet cloths on all exposed areas of grout for a minimum of 6 hours.

- After 6 hours, remove cloths and apply membrane forming curing compound.

# END OF SECTION